## Dashboard
DG Service-Call Dashboard Explore sheet: use slicers there for slice-and-dice; refresh pivot after new data.
From | 2026-06-01
To | 2026-07-22
Period | Jun 1 to Jul 22
Checks needing review | 2
Timeline - pick cause OR group:
Timeline cause | Doors
Date basis | Call date

## Explore
Slice-and-dice. Slicers filter the chart and table live. Right-click Refresh after adding Summary rows.
Row Labels | Count of Work Order
False Alarm | 1
Grand Total | 1
This shape represents a slicer. Slicers can be used in at least Excel 2010. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2003 or earlier, the slicer cannot be used.
This shape represents a slicer. Slicers can be used in at least Excel 2010. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2003 or earlier, the slicer cannot be used.
This shape represents a slicer. Slicers can be used in at least Excel 2010. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2003 or earlier, the slicer cannot be used.
This shape represents a slicer. Slicers can be used in at least Excel 2010. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2003 or earlier, the slicer cannot be used.
This shape represents a slicer. Slicers can be used in at least Excel 2010. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2003 or earlier, the slicer cannot be used.

## Data Checks (hidden)
Check | Count | Status | What to fix | Formula scope
Heatmap classified line reconciliation | 84 | Review | Heatmap sum must equal classified Summary lines in the active Dashboard date window. | Heatmap Calc vs Summary
Root causes not in Settings | 0 | OK | Pick a valid Root Cause from the dropdown. | Summary vs Settings
Clean-point daily chart reconciliation | 32 | OK | Timeline sum must equal selected cause/group rows in the Dashboard call-date window; basis only changes plotted dates. | Timeline Calc vs Summary
Explore pivot grand total reconciliation | 1 | Review | Clear Explore slicers and refresh pivot if this shows Review. | Explore Pivot vs Summary
Gap histogram reconciliation | 32 | OK | Gap histogram n must equal direct in-scope gap-bearing Summary rows. | Timeline Calc vs Summary

## Heatmap Calc
Cause x week heatmap - source range for the linked picture on Dashboard. Format HERE, not on the picture.
Issues by root cause x commission date week (Jun 1 to Jul 22)
| 2026-03-02 | 2026-03-09 | 2026-03-16 | 2026-03-23 | 2026-03-30 | 2026-04-06 | 2026-04-13 | 2026-04-20 | 2026-04-27 | 2026-05-04 | 2026-05-11 | 2026-05-18 | 2026-05-25 | 2026-06-01 | 2026-06-08 | 2026-06-15 | 2026-06-22 | 2026-06-29 | 2026-07-06
Ref. leak/ Low charge | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0
Door Torque | 0 | 0 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0
Door Gasket | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Door frame heater | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Door Torsion rod | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
Door not closed (Overnight) | 1 | 2 | 1 | 1 | 0 | 0 | 2 | 1 | 0 | 2 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1
Door - general | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
Drain tube blocked | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
Wrong / Loose wiring | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
Communication problem | 0 | 0 | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0
High Store RH | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2 | 0 | 1 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2
Enclosure Seal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Component Failure | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0
Defrost Sync | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
False Alarm | 0 | 0 | 1 | 2 | 0 | 0 | 2 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 2 | 2 | 0 | 0
Setpoint change | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
Overstocking | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 0
Double defrost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Return Air blocked | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Unidentified air leak | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Freedom | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1
Heavy case load | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Installation issue | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 1 | 0 | 0 | 2
Unknown | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3 | 1 | 0
Program change - Hussmann | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wrong program | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
Heatmap date basis | 2026-03-02: Commission date
Heatmap first week | 2026-03-02: 2026-03-02
Heatmap first plotted date | 2026-03-02: 2026-03-03

## Interventions
Intervention log - one row per clean point / fix action. Drives the clean-point lines chart. Settings' Clean-Point Date column still drives the after/before charts.
Root Cause | Date | Label
Ref. leak/ Low charge | 2026-04-20 | Clean point
Door Torque | 2026-06-05 | Clean point
Door Gasket | 2026-06-05 | Clean point
Door frame heater | 2026-06-05 | Clean point
Door Torsion rod | 2026-06-05 | Clean point
Door not closed (Overnight) | 2026-06-05 | Clean point
Door - general | 2026-06-05 | Clean point
Drain tube blocked | 2026-07-10 | Clean point
Wrong / Loose wiring | 2026-03-27 | Clean point
Communication problem | 2026-06-18 | Clean point
High Store RH | 2026-05-29 | Clean point
Enclosure Seal | 2026-04-23 | Clean point
Component Failure | 2026-03-01 | Clean point
Defrost Sync | 2026-06-12 | Clean point
False Alarm | 2026-05-22 | Clean point
Setpoint change | 2026-03-16 | Clean point
Overstocking | 2026-05-29 | Clean point
Double defrost | 2026-05-29 | Clean point
Return Air blocked | 2026-05-29 | Clean point
Unidentified air leak | 2026-06-16 | Clean point
Freedom | 2026-03-01 | Clean point
Heavy case load | 2026-05-29 | Clean point
Installation issue | 2026-05-29 | Clean point
Unknown | 2026-03-01 | Clean point
Program change - Hussmann | 2026-05-29 | Clean point

## Timeline Calc (hidden)
Daily clean-point timeline source. Pickers live on Dashboard!B83:B84. | [16 empty] | Gap histogram source - shares tl_cause
Cause | Doors
Basis | Call date
| Doors - issues by Call date, with clean points (Jun 1 to Jul 22) | [15 empty] | Bucket | Lo | Hi | Count |  | Metric | Value
[17 empty] | 0-7 days | 0 | 7 | 4 |  | n | 32
[17 empty] | 8-14 days | 8 | 14 | 1 |  | median | 64.5
Date | Issues | Clean Point 1 | Clean Point 2 | Clean Point 3 | CP Date 1 | CP Date 2 | CP Date 3 | CP Label 1 | CP Label 2 | CP Label 3 | Ceiling | Cause | Group | CP date | Pick list raw | Pick list | 15-30 days | 15 | 30 | 2 | In-scope gap | title | Doors issues - days from Store opening to service call
2026-06-01 | 0 | #N/A | #N/A | #N/A | 2026-06-05 | 2026-07-17 | 0 | Clean point 1 - Jun 5 | Clean point 2 - Jul 17 |  | 4 | Ref. leak/ Low charge | Ref. leak/ Low charge | 46132 | Ref. leak/ Low charge | Ref. leak/ Low charge | 31-60 days | 31 | 60 | 8
2026-06-02 | 1 | #N/A | #N/A | #N/A | [7 empty] | Door Torque | Doors | 46178 | Door Torque | Door Torque | 61-90 days | 61 | 90 | 11
2026-06-03 | 0 | #N/A | #N/A | #N/A | [7 empty] | Door Gasket | Doors | 46178 | Door Gasket | Door Gasket | 90+ days | 91 | 100000 | 6
2026-06-04 | 0 | #N/A | #N/A | #N/A | [7 empty] | Door frame heater | Doors | 46178 | Door frame heater | Door frame heater
2026-06-05 | 0 | 1 | #N/A | #N/A | [7 empty] | Door Torsion rod | Doors | 46178 | Door Torsion rod | Door Torsion rod
2026-06-06 | 0 | #N/A | #N/A | #N/A | [7 empty] | Door not closed (Overnight) | Doors | 46178 | Door not closed (Overnight) | Door not closed (Overnight)
2026-06-07 | 1 | #N/A | #N/A | #N/A | [7 empty] | Door - general | Doors | 46178 | Door - general | Door - general
2026-06-08 | 1 | #N/A | #N/A | #N/A | [7 empty] | Drain tube blocked | Drain tube blocked | 46213 | Drain tube blocked | Drain tube blocked
2026-06-09 | 1 | #N/A | #N/A | #N/A | [7 empty] | Wrong / Loose wiring | Wrong / Loose wiring | 46108 | Wrong / Loose wiring | Wrong / Loose wiring
2026-06-10 | 2 | #N/A | #N/A | #N/A | [7 empty] | Communication problem | Communication problem | 46191 | Communication problem | Communication problem
2026-06-11 | 2 | #N/A | #N/A | #N/A | [7 empty] | High Store RH | High Store RH | 46171 | High Store RH | High Store RH
2026-06-12 | 0 | #N/A | #N/A | #N/A | [7 empty] | Enclosure Seal | Enclosure Seal | 46135 | Enclosure Seal | Enclosure Seal
2026-06-13 | 0 | #N/A | #N/A | #N/A | [7 empty] | Component Failure | Component Failure | 46082 | Component Failure | Component Failure
2026-06-14 | 0 | #N/A | #N/A | #N/A | [7 empty] | Defrost Sync | Defrost Sync | 46185 | Defrost Sync | Defrost Sync
2026-06-15 | 1 | #N/A | #N/A | #N/A | [7 empty] | False Alarm | False Alarm | 46164 | False Alarm | False Alarm
2026-06-16 | 1 | #N/A | #N/A | #N/A | [7 empty] | Setpoint change | Setpoint change | 46097 | Setpoint change | Setpoint change
2026-06-17 | 0 | #N/A | #N/A | #N/A | [7 empty] | Overstocking | Overstocking | 46171 | Overstocking | Overstocking
2026-06-18 | 2 | #N/A | #N/A | #N/A | [7 empty] | Double defrost | Double defrost | 46171 | Double defrost | Double defrost
2026-06-19 | 0 | #N/A | #N/A | #N/A | [7 empty] | Return Air blocked | Return Air blocked | 46171 | Return Air blocked | Return Air blocked
2026-06-20 | 0 | #N/A | #N/A | #N/A | [7 empty] | Unidentified air leak | Unidentified air leak | 46189 | Unidentified air leak | Unidentified air leak
2026-06-21 | 0 | #N/A | #N/A | #N/A | [7 empty] | Freedom | Freedom | 46082 | Freedom | Freedom
2026-06-22 | 1 | #N/A | #N/A | #N/A | [7 empty] | Heavy case load | Heavy case load | 46171 | Heavy case load | Heavy case load
2026-06-23 | 0 | #N/A | #N/A | #N/A | [7 empty] | Installation issue | Installation issue | 46171 | Installation issue | Installation issue
2026-06-24 | 0 | #N/A | #N/A | #N/A | [7 empty] | Unknown | Unknown | 46082 | Unknown | Unknown
2026-06-25 | 2 | #N/A | #N/A | #N/A | [7 empty] | Program change - Hussmann | Program change - Hussmann | 46171 | Program change - Hussmann | Program change - Hussmann
2026-06-26 | 1 | #N/A | #N/A | #N/A | [7 empty] | Wrong program | Wrong program | 0 | Wrong program | Wrong program
2026-06-27 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0 |  | Doors
2026-06-28 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-06-29 | 1 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-06-30 | 2 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-07-01 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-07-02 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-07-03 | 3 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-07-04 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-07-05 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-07-06 | 3 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-07-07 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-07-08 | 1 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-07-09 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-07-10 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-07-11 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-07-12 | 1 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-07-13 | 1 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-07-14 | 1 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-07-15 | 1 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-07-16 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-07-17 | 1 | #N/A | 1 | #N/A | [9 empty] | 0
2026-07-18 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-07-19 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-07-20 | 1 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-07-21 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-07-22 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-07-23 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-07-24 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-07-25 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-07-26 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-07-27 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-07-28 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-07-29 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-07-30 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-07-31 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-08-01 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-08-02 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-08-03 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-08-04 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-08-05 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-08-06 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-08-07 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-08-08 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-08-09 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-08-10 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-08-11 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-08-12 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-08-13 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-08-14 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-08-15 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-08-16 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-08-17 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0 | [6 empty] | 31
2026-08-18 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-08-19 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-08-20 | 0 | #N/A | #N/A | #N/A | [7 empty] | Ref. leak/ Low charge | Ref. leak/ Low charge | 0
2026-08-21 | 0 | #N/A | #N/A | #N/A | [7 empty] | Door Torque | Doors | 46220 | Doors
2026-08-22 | 0 | #N/A | #N/A | #N/A | [7 empty] | Door Gasket | Doors | 46220 | [6 empty] | 14
2026-08-23 | 0 | #N/A | #N/A | #N/A | [7 empty] | Door frame heater | Doors | 46220
2026-08-24 | 0 | #N/A | #N/A | #N/A | [7 empty] | Door Torsion rod | Doors | 46220 | [6 empty] | 56
2026-08-25 | 0 | #N/A | #N/A | #N/A | [7 empty] | Door not closed (Overnight) | Doors | 46220
2026-08-26 | 0 | #N/A | #N/A | #N/A | [7 empty] | Door - general | Doors | 0 | [6 empty] | 83
2026-08-27 | 0 | #N/A | #N/A | #N/A | [7 empty] | Drain tube blocked | Drain tube blocked | 0
2026-08-28 | 0 | #N/A | #N/A | #N/A | [7 empty] | Wrong / Loose wiring | Wrong / Loose wiring | 0 | [6 empty] | 75
2026-08-29 | 0 | #N/A | #N/A | #N/A | [7 empty] | Communication problem | Communication problem | 0
2026-08-30 | 0 | #N/A | #N/A | #N/A | [7 empty] | High Store RH | High Store RH | 0
2026-08-31 | 0 | #N/A | #N/A | #N/A | [7 empty] | Enclosure Seal | Enclosure Seal | 0
2026-09-01 | 0 | #N/A | #N/A | #N/A | [7 empty] | Component Failure | Component Failure | 0
2026-09-02 | 0 | #N/A | #N/A | #N/A | [7 empty] | Defrost Sync | Defrost Sync | 0
2026-09-03 | 0 | #N/A | #N/A | #N/A | [7 empty] | False Alarm | False Alarm | 0
2026-09-04 | 0 | #N/A | #N/A | #N/A | [7 empty] | Setpoint change | Setpoint change | 0
2026-09-05 | 0 | #N/A | #N/A | #N/A | [7 empty] | Overstocking | Overstocking | 0 | [6 empty] | 85
2026-09-06 | 0 | #N/A | #N/A | #N/A | [7 empty] | Double defrost | Double defrost | 0
2026-09-07 | 0 | #N/A | #N/A | #N/A | [7 empty] | Return Air blocked | Return Air blocked | 0 | [6 empty] | 78
2026-09-08 | 0 | #N/A | #N/A | #N/A | [7 empty] | Unidentified air leak | Unidentified air leak | 0 | [6 empty] | 78
2026-09-09 | 0 | #N/A | #N/A | #N/A | [7 empty] | Freedom | Freedom | 0
2026-09-10 | 0 | #N/A | #N/A | #N/A | [7 empty] | Heavy case load | Heavy case load | 0
2026-09-11 | 0 | #N/A | #N/A | #N/A | [7 empty] | Installation issue | Installation issue | 0 | [6 empty] | 38
2026-09-12 | 0 | #N/A | #N/A | #N/A | [7 empty] | Unknown | Unknown | 0
2026-09-13 | 0 | #N/A | #N/A | #N/A | [7 empty] | Program change - Hussmann | Program change - Hussmann | 0
2026-09-14 | 0 | #N/A | #N/A | #N/A | [7 empty] | Wrong program | Wrong program | 0 | [6 empty] | 29
2026-09-15 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-09-16 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0 | [6 empty] | 64
2026-09-17 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-09-18 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-09-19 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-09-20 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0 | [6 empty] | 5
2026-09-21 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-09-22 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0 | [6 empty] | 92
2026-09-23 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-09-24 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0 | [6 empty] | 65
2026-09-25 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-09-26 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0 | [6 empty] | 83
2026-09-27 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-09-28 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0 | [6 empty] | 40
2026-09-29 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0 | [6 empty] | 103
2026-09-30 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0 | [6 empty] | 60
2026-10-01 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-10-02 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0 | [6 empty] | 125
2026-10-03 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0 | [6 empty] | 115
2026-10-04 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-10-05 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0 | [6 empty] | 16
2026-10-06 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-10-07 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0 | [6 empty] | 3
2026-10-08 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-10-09 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-10-10 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-10-11 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-10-12 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0 | [6 empty] | 69
2026-10-13 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-10-14 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0 | [6 empty] | 42
2026-10-15 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0 | [6 empty] | 110
2026-10-16 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-10-17 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-10-18 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-10-19 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0 | [6 empty] | 42
2026-10-20 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-10-21 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0 | [6 empty] | 76
2026-10-22 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-10-23 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-10-24 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0 | [6 empty] | 33
2026-10-25 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-10-26 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-10-27 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0 | [6 empty] | 4
2026-10-28 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-10-29 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-10-30 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-10-31 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-11-01 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-11-02 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-11-03 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-11-04 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-11-05 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-11-06 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0 | [6 empty] | 97
2026-11-07 | 0 | #N/A | #N/A | #N/A | [9 empty] | 0
2026-11-08 | 0 | #N/A | #N/A | #N/A | [7 empty] | Ref. leak/ Low charge | Ref. leak/ Low charge | 0
2026-11-09 | 0 | #N/A | #N/A | #N/A | [7 empty] | Door Torque | Doors | 0 | [6 empty] | 1
2026-11-10 | 0 | #N/A | #N/A | #N/A | [7 empty] | Door Gasket | Doors | 0
2026-11-11 | 0 | #N/A | #N/A | #N/A | [7 empty] | Door frame heater | Doors | 0
2026-11-12 | 0 | #N/A | #N/A | #N/A | [7 empty] | Door Torsion rod | Doors | 0 | [6 empty] | 69
2026-11-13 | 0 | #N/A | #N/A | #N/A | [7 empty] | Door not closed (Overnight) | Doors | 0
2026-11-14 | 0 | #N/A | #N/A | #N/A | [7 empty] | Door - general | Doors | 0
2026-11-15 | 0 | #N/A | #N/A | #N/A | [7 empty] | Drain tube blocked | Drain tube blocked | 0
2026-11-16 | 0 | #N/A | #N/A | #N/A | [7 empty] | Wrong / Loose wiring | Wrong / Loose wiring | 0
2026-11-17 | 0 | #N/A | #N/A | #N/A | [7 empty] | Communication problem | Communication problem | 0
2026-11-18 | 0 | #N/A | #N/A | #N/A | [7 empty] | High Store RH | High Store RH | 0
2026-11-19 | 0 | #N/A | #N/A | #N/A | [7 empty] | Enclosure Seal | Enclosure Seal | 0
2026-11-20 | 0 | #N/A | #N/A | #N/A | [7 empty] | Component Failure | Component Failure | 0
2026-11-21 | 0 | #N/A | #N/A | #N/A | [7 empty] | Defrost Sync | Defrost Sync | 0
2026-11-22 | 0 | #N/A | #N/A | #N/A | [7 empty] | False Alarm | False Alarm | 0
2026-11-23 | 0 | #N/A | #N/A | #N/A | [7 empty] | Setpoint change | Setpoint change | 0
2026-11-24 | 0 | #N/A | #N/A | #N/A | [7 empty] | Overstocking | Overstocking | 0
2026-11-25 | 0 | #N/A | #N/A | #N/A | [7 empty] | Double defrost | Double defrost | 0
2026-11-26 | 0 | #N/A | #N/A | #N/A | [7 empty] | Return Air blocked | Return Air blocked | 0
2026-11-27 | 0 | #N/A | #N/A | #N/A | [7 empty] | Unidentified air leak | Unidentified air leak | 0
2026-11-28 | 0 | #N/A | #N/A | #N/A | [7 empty] | Freedom | Freedom | 0
2026-11-29 | 0 | #N/A | #N/A | #N/A | [7 empty] | Heavy case load | Heavy case load | 0
2026-11-30 | 0 | #N/A | #N/A | #N/A | [7 empty] | Installation issue | Installation issue | 0
2026-12-01 | 0 | #N/A | #N/A | #N/A | [7 empty] | Unknown | Unknown | 0
[12 empty] | Program change - Hussmann | Program change - Hussmann | 0
[12 empty] | Wrong program | Wrong program | 0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0

## Summary
Call Date | Work Order | Store | Commission Date | Root Cause | Notes | After Clean Point | Case Serial (from Raw) | Column1 | Store connect/ FEXA | Group | Nomenclature | Gap (days)
2026-03-13 09:26 | WO-0532764 | Dollar General #22515 | 2026-03-09 | Door Torque | Tech found door torque issue and adjusted it | No | RMN5MA/MY26B013859 |  | CALLER | Doors | RMN5MA | 4
2026-03-13 09:26 | WO-0532764 | Dollar General #22515 | 2026-03-09 | Drain tube blocked |  | No | RMN5MA/MY26B013859 |  | CALLER | Drain tube blocked | RMN5MA | 4
2026-03-11 08:16 | WO-0531272 | Dollar General #21606 | 2026-03-03 | Drain tube blocked |  | No | RMN5MA/MY26B013853 |  | FEXA | Drain tube blocked | RMN5MA | 8
2026-03-11 08:16 | WO-0531272 | Dollar General #21606 | 2026-03-03 | High Store RH |  | No | RMN5MA/MY26B013853 |  | FEXA | High Store RH | RMN5MA | 8
2026-03-21 09:20 | WO-0536941 | Dollar General #20582 | 2026-03-17 | Ref. leak/ Low charge |  | No | RLN3MA/MY26B014956, LEFT ~ RLN2MA/ MY26B016476, LEFT |  | STORE CONNECT | Ref. leak/ Low charge | RLN2MA | 4
2026-03-21 09:20 | WO-0536941 | Dollar General #20582 | 2026-03-17 | Enclosure Seal |  | No | RLN3MA/MY26B014956, LEFT ~ RLN2MA/ MY26B016476, LEFT |  | STORE CONNECT | Enclosure Seal | RLN2MA | 4
2026-03-19 12:57 | WO-0536090 | Dollar General #04117 | 2026-03-17 | Communication problem | Microblock | No |  |  | FEXA | Communication problem |  | 2
2026-03-30 06:28 | WO-0541495 | Dollar General #22149 | 2026-03-11 | Component Failure |  | Yes | RMN5MA/MY26B013852 RLN3MA/MY26B013833 ~ RLN2MA/MY26B013807 ~ RFMN4/MY21G066701 |  | STORE CONNECT | Component Failure | RLN2MA | 19
2026-03-30 06:24 | WO-0541490 | Dollar General #6099 | 2026-03-17 | Communication problem | Microblock | No | N/A |  | STORE CONNECT | Communication problem | other | 13
2026-03-30 07:41 | WO-0541572 | Dollar General 22799 | 2026-03-18 | Wrong program |  | No | RLN2MA/MY26B014943 |  | FEXA | Wrong program | RLN2MA | 12
2026-03-30 09:04 | WO-0541656 | DOLLAR GENERAL #10369 | 2026-03-25 | Wrong / Loose wiring |  | No | RMN5MA/MY26B016046, LEFT |  | STORE CONNECT | Wrong / Loose wiring | RMN5MA | 5
2026-04-02 14:45 | WO-0545426 | Dollar General #12879 | 2026-03-25 | Wrong / Loose wiring |  | No | RMN5MA/MY26B016549, LEFT |  | STORE CONNECT | Wrong / Loose wiring | RMN5MA | 8
2026-04-02 15:17 | WO-0545463 | DOLLAR GENERAL #10369 | 2026-03-25 | Wrong / Loose wiring |  | No | RMN4MA/MY26B016036, LEFT |  | INTERNAL | Wrong / Loose wiring | RMN4MA | 8
2026-04-04 18:29 | WO-0546538 | Dollar General #20876 | 2026-03-31 | High Store RH |  | No | RLN2MA/MY26B013812 |  | STORE CONNECT | High Store RH | RLN2MA | 4
2026-04-06 13:09 | WO-0547346 | Dollar General #6827 | 2026-03-05 | False Alarm |  | No | RLN2MA/MY26b013811 ~ RLN3MA/MY26B013832 |  | STORE CONNECT | False Alarm | RLN2MA | 32
2026-04-08 09:25 | WO-0548436 | Dollar General #3270 | 2026-04-08 | Component Failure |  | Yes | MY26B016515 |  | STORE CONNECT | Component Failure | other | 0
2026-04-07 14:40 | WO-0548123 | Dollar General #14858 | 2026-03-16 | Door Torque | Tech found door torque issue and adjusted it | No | RMN5MA/MY26B016546, LEFT |  | STORE CONNECT | Doors | RMN5MA | 22
2026-04-07 14:40 | WO-0548123 | Dollar General #14858 | 2026-03-16 | Wrong / Loose wiring |  | No | RMN5MA/MY26B016546, LEFT |  | STORE CONNECT | Wrong / Loose wiring | RMN5MA | 22
2026-04-09 12:22 | WO-0549298 | Dollar General #21016 | 2026-04-07 | Communication problem |  | No | RLN2MA/MY26B015995 |  | STORE CONNECT | Communication problem | RLN2MA | 2
2026-04-10 13:46 | WO-0549951 | Dollar General #21223 | 2026-04-08 | Ref. leak/ Low charge | Microblock | No |  |  | FEXA | Ref. leak/ Low charge |  | 2
2026-04-08 15:16 | WO-0548822 | Dollar General #13338 | 2026-03-11 | Component Failure |  | Yes | RLN2MA/MY26B013807, RLN3MA/MY26B013833, RMN5MA/MY26B013852 |  | FEXA | Component Failure | RLN2MA | 28
2026-04-09 12:01 | WO-0549280 | Dollar General #20407 | 2026-04-07 | Ref. leak/ Low charge |  | No | RLN3MA/MY26B016017, RIGHT |  | STORE CONNECT | Ref. leak/ Low charge | RLN3MA | 2
2026-04-09 12:01 | WO-0549280 | Dollar General #20407 | 2026-04-07 | Defrost Sync |  | No | RLN3MA/MY26B016017, RIGHT |  | STORE CONNECT | Defrost Sync | RLN3MA | 2
2026-04-13 10:23 | WO-0551078 | Dollar General #14858 | 2026-03-16 | Return Air blocked |  | No | RLN2MA/MY26B016475, LEFT |  | STORE CONNECT | Return Air blocked | RLN2MA | 28
2026-04-14 09:12 | WO-0551833 | Dollar General #21016 | 2026-04-07 | Unknown |  | Yes | RMN3MA/MY26B016499 |  | STORE CONNECT | Unknown | RMN3MA | 7
2026-04-14 12:17 | WO-0552039 | Dollar General #14104 | 2026-03-24 | Freedom |  | Yes | RLN2MA/MY26B015990 Left |  | FEXA | Freedom | RLN2MA | 21
2026-04-14 12:29 | WO-0552056 | Dollar General #22286 | 2026-03-18 | False Alarm |  | No | RLN2MA/MY26B014938, LEFT |  | FEXA | False Alarm | RLN2MA | 27
2026-04-14 12:36 | WO-0552063 | Dollar General #20876 | 2026-03-31 | High Store RH |  | No | RLN2MA/MY26B013812 |  | FEXA | High Store RH | RLN2MA | 14
2026-04-14 12:50 | WO-0552080 | Dollar General #22281 | 2026-04-06 | Defrost Sync |  | No | RLN3MA/MY26B016019, RIGHT |  | STORE CONNECT | Defrost Sync | RLN3MA | 8
2026-04-14 12:50 | WO-0552080 | Dollar General #22281 | 2026-04-06 | False Alarm |  | No | RLN3MA/MY26B016019, RIGHT |  | STORE CONNECT | False Alarm | RLN3MA | 8
2026-04-14 13:00 | WO-0552093 | Dollar General #3270 | 2026-04-08 | Ref. leak/ Low charge |  | No | RLN3MA/MY26B016488, RIGHT |  | FEXA | Ref. leak/ Low charge | RLN3MA | 6
2026-04-14 13:24 | WO-0552123 | Dollar General #22613 | 2026-03-18 | Wrong / Loose wiring |  | No | RLN2MA/MY26B014941 |  | STORE CONNECT | Wrong / Loose wiring | RLN2MA | 27
2026-04-14 13:29 | WO-0552129 | Dollar General #14858 | 2026-03-16 | Door - general |  | No | RLN3MA/MY26B016004 |  | STORE CONNECT | Doors | RLN3MA | 29
2026-04-14 13:29 | WO-0552129 | Dollar General #14858 | 2026-03-16 | Defrost Sync |  | No | RLN3MA/MY26B016004 |  | STORE CONNECT | Defrost Sync | RLN3MA | 29
2026-04-15 05:58 | WO-0552473 | Dollar General #22930 | 2026-04-16 | Ref. leak/ Low charge |  | No | RMN3MA/MY26C025316 |  | STORE CONNECT | Ref. leak/ Low charge | RMN3MA | -1
2026-04-15 07:43 | WO-0552572 | Dollar General #21377 | 2026-03-12 | Door - general |  | No | RLN2MA/MY26B013804, LEFT |  | STORE CONNECT/FEXA | Doors | RLN2MA | 34
2026-04-16 10:55 | WO-0553537 | Dollar General #21135 | 2026-03-25 | Door Torque | No comments from tech. but looking at the data, this is a door not closing issue which is most likely because of door torque | No | RMN3MA/MY26b016480 |  | STORE CONNECT | Doors | RMN3MA | 22
2026-04-16 10:55 | WO-0553537 | Dollar General #21135 | 2026-03-25 | Drain tube blocked |  | No | RMN3MA/MY26b016480 |  | STORE CONNECT | Drain tube blocked | RMN3MA | 22
2026-04-18 09:04 | WO-0554820 | Dollar General #22982 | 2026-04-14 | Door - general |  | No | RLN4MA/MY26B014967, LEFT |  | FEXA | Doors | RLN4MA | 4
2026-04-21 09:53 | WO-0556537 | Dollar General #22930 | 2026-04-16 | Enclosure Seal |  | No | RLN4MA/MY26B014974 |  | STORE CONNECT | Enclosure Seal | RLN4MA | 5
2026-04-21 09:53 | WO-0556537 | Dollar General #22930 | 2026-04-16 | Component Failure |  | Yes | RLN4MA/MY26B014974 |  | STORE CONNECT | Component Failure | RLN4MA | 5
2026-04-23 06:23 | WO-0557805 | Dollar General #21130 | 2026-04-13 | Installation issue |  | No | RLN3MA/MY26C019887 |  | FEXA | Installation issue | RLN3MA | 10
2026-04-22 05:52 | WO-0557035 | Dollar General #20876 | 2026-03-31 | Communication problem |  | No | RMN4MA/MY26B013850, RLN3MA/MY26B013819, RNL2MA/MY26B013812, RMN3MA/MY26B013772, RMN3MA/MY26B013770, RFMN5/MY19M090256, RFMN5/MY19M090255, RFLN4/MY19M090238, RFLN4/MY19M090237, RFLN3/MY19M090226 |  | STORE CONNECT | Communication problem | RLN3MA | 22
2026-04-22 05:52 | WO-0557035 | Dollar General #20876 | 2026-03-31 | High Store RH |  | No | RMN4MA/MY26B013850, RLN3MA/MY26B013819, RNL2MA/MY26B013812, RMN3MA/MY26B013772, RMN3MA/MY26B013770, RFMN5/MY19M090256, RFMN5/MY19M090255, RFLN4/MY19M090238, RFLN4/MY19M090237, RFLN3/MY19M090226 |  | STORE CONNECT | High Store RH | RLN3MA | 22
2026-04-27 05:25 | WO-0559894 | Dollar General #21342 | 2026-04-10 | Ref. leak/ Low charge |  | No | RLN3MA/MY26B016018, LEFT |  | FEXA | Ref. leak/ Low charge | RLN3MA | 17
2026-04-27 07:37 | WO-0560039 | Dollar General #20582 | 2026-03-17 | Enclosure Seal |  | No | RLN2MA/MY26B016475 |  | FEXA | Enclosure Seal | RLN2MA | 41
2026-04-27 07:37 | WO-0560039 | Dollar General #20582 | 2026-03-17 | Double defrost |  | No | RLN2MA/MY26B016475 |  | FEXA | Double defrost | RLN2MA | 41
2026-05-02 07:40 | WO-0563528 | Dollar General #13396 | 2026-04-29 | Communication problem |  | No | RLN2MA MY26B016003 |  | STORE CONNECT | Communication problem | RLN2MA | 3
2026-05-05 | WO-0564924 | Dollar General #13631 | 2026-05-05 | False Alarm |  | No | RMN4MA/MY26D028116 |  | STORE CONNECT | False Alarm | RMN4MA | 0
2026-05-06 | WO-0565337 | Dollar General #21606 | 2026-03-03 | Door - general |  | No | RLN3MA MY26B013826 |  | STORE CONNECT | Doors | RLN3MA | 64
2026-05-06 | WO-0565337 | Dollar General #21606 | 2026-03-03 | Defrost Sync |  | No | RLN3MA MY26B013826 |  | STORE CONNECT | Defrost Sync | RLN3MA | 64
2026-05-05 10:51 | WO-0564555 | Dollar General #10339 | 2026-04-29 | Overstocking |  | No | RLN2MA MY26B016459 |  | FEXA | Overstocking | RLN2MA | 6
2026-05-08 09:11 | WO-0566374 | Dollar General #20639 | 2026-04-13 | Door Torque | Tech found door torque issue and adjusted it | No | RLN3MA/MY26B016016 |  | STORE CONNECT | Doors | RLN3MA | 25
2026-05-10 03:45 | WO-0567300 | Dollar General #22864 | 2026-03-24 | Wrong program |  | No | RLN3MA/MY26B014958 |  | FEXA | Wrong program | RLN3MA | 47
2026-05-12 11:46 | WO-0568428 | Dollar General #22613 | 2026-03-18 | Ref. leak/ Low charge |  | No | RLN2MA/MY26B014941 |  | FEXA | Ref. leak/ Low charge | RLN2MA | 55
2026-05-12 11:49 | WO-0568430 | Dollar General #14858 | 2026-03-16 | Ref. leak/ Low charge |  | No | RLN3MA/MY26B016004 |  | STORE CONNECT/ FEXA | Ref. leak/ Low charge | RLN3MA | 57
2026-05-12 04:15 | WO-0568634 | Dollar General #3270 | 2026-04-08 | Ref. leak/ Low charge |  | No | RLN3MA/ MY26B016488, CENTER/RIGHT |  | FEXA | Ref. leak/ Low charge | RLN3MA | 34
2026-05-12 11:38 | WO-0568415 | Dollar General #14104 | 2026-03-24 | Unidentified air leak |  | No | RLN2MA/MY26B015990 |  | FEXA | Unidentified air leak | RLN2MA | 49
2026-05-12 11:38 | WO-0568415 | Dollar General #14104 | 2026-03-24 | Heavy case load |  | No | RLN2MA/MY26B015990 |  | FEXA | Heavy case load | RLN2MA | 49
2026-05-12 11:53 | WO-0568437 | Dollar General #22286 | 2026-03-18 | Unidentified air leak |  | No | RLN2MA/MY26B014938 |  | STORE CONNECT | Unidentified air leak | RLN2MA | 55
2026-05-13 08:13 | WO-0568891 | Dollar General #21375 | 2026-03-10 | Wrong program |  | No | RLN3MA/MY26B013828 |  | FEXA | Wrong program | RLN3MA | 64
2026-05-13 08:38 | WO-0569146 | Dollar General #21130 | 2026-04-13 | Drain tube blocked |  | No | RLN3MA/MY26C019887 |  | FEXA | Drain tube blocked | RLN3MA | 30
2026-05-17 08:30 | WO-0571130 | Dollar General #20597 | 2026-04-22 | Door frame heater |  | No | RLN3MA/MY26B016493 |  | SUZANNE | Doors | RLN3MA | 25
2026-05-16 10:06 | WO-0570321 | Dollar General #21778 | 2026-05-06 | Drain tube blocked |  | No | RLN3MA/MY26D028107 |  | FEXA | Drain tube blocked | RLN3MA | 10
2026-05-15 02:48 | WO-0570508 | Dollar General #14928 | 2026-05-12 | Door - general |  | No | RLN2MA/MY26D02809, RLN3MA/MY26D03141 |  | FEXA | Doors | RLN2MA | 3
2026-05-26 12:31 | WO-0578039 | Dollar General #12799 |  | Installation issue | Disaster - move cases | No |  |  | STORE CONNECT | Installation issue
2026-05-22 07:57 | WO-0575409 | Dollar General #10339 | 2026-04-29 | Drain tube blocked |  | No | RLN2MA/MY26B016459 (same case from 5/5) |  | FEXA | Drain tube blocked | RLN2MA | 23
2026-05-22 06:03 | WO-0575297 | Dollar General #19997 | 2026-04-30 | Door Torque | Tech found door torque issue and adjusted it | No | RMN4MA/MY26B016517 |  | FEXA | Doors | RMN4MA | 22
2026-05-20 12:41 | WO-0573996 | Dollar General #20107 | 2026-05-06 | Program change - Hussmann |  | No | RLN2MA/MY26B015992 (not pulling up in PP) |  | STORE CONNECT | Program change - Hussmann | RLN2MA | 14
2026-05-20 02:19 | WO-0574005 | Dollar General #21223 | 2026-04-08 | Installation issue |  | No | RLN2MA MY26B014946 |  | ANDREW MILLER | Installation issue | RLN2MA | 42
2026-05-18 05:55 | WO-0572389 | Dollar General #7231 |  | Freedom |  | No |  |  | FEXA | Freedom
2026-05-29 09:34 | WO-0580073 | Dollar General #20582 | 2026-03-17 | Door Torque | Tech found door torque issue and adjusted it | No | RLN3MA/MY26B014956 |  | STORE CONNECT | Doors | RLN3MA | 73
2026-05-30 04:57 | WO-0580974 | Dollar General #21415 | 2026-05-28 | Freedom | NA | Yes |  |  | FEXA | Freedom |  | 2
2026-05-30 03:30 | WO-0580946 | Dollar General #6372 | 2026-04-14 | Unknown | All MB cases in one store | Yes | RLN3MA/MY26C019883, RMN4MA/MY26B016031 |  | STORE CONNECT | Unknown | RLN3MA | 46
2026-05-29 04:37 | WO-0580512 | Dollar General #14347 | 2026-04-22 | Drain tube blocked | No case noms. But before clean point | No |  |  | FEXA | Drain tube blocked |  | 37
2026-05-29 04:37 | WO-0580512 | Dollar General #14347 | 2026-04-22 | Freedom | NA | Yes |  |  | FEXA | Freedom |  | 37
2026-06-08 12:53 | WO-0586550 | Dollar General #2600 | 2026-05-27 | Setpoint change | One unit was set 5 degress higher than the other. | Yes | RMN3MA/MY26D026820 |  | FEXA | Setpoint change | RMN3MA | 12
2026-06-07 08:32 | WO-0585699 | Dollar General #3277 | 2026-05-07 | Door not closed (Overnight) | Per data the door was open. But tech has cleaned the evaporator to deiced | No | RLN3MA/MY26D028108 |  | STORE CONNECT | Doors | RLN3MA | 31
2026-06-05 04:26 | WO-0584971 | Dollar General #1247 | 2026-06-01 | Ref. leak/ Low charge | Cassettes were replaced. Tech pierced cassettes and figured they are low on refrigerant | Yes | RLN4MA/MY26C019909 |  | FEXA | Ref. leak/ Low charge | RLN4MA | 4
2026-06-04 10:30 | WO-0583967 | Dollar General #21342 | 2026-04-10 | Freedom | Found issue with pumps on freedom cases | Yes | RLN2MA/MY26C019880 |  | RPM/ROB S. | Freedom | RLN2MA | 55
2026-06-03 22:14 | WO-0583750 | Dollar General #1247 | 2026-06-01 | Ref. leak/ Low charge | Tech notes about cassette replacement. No more details. | Yes | RMN4MA/MY26B016036 |  | FEXA | Ref. leak/ Low charge | RMN4MA | 2
2026-06-03 09:41 | WO-0583216 | Dollar General #20336 | 2026-04-14 | False Alarm | Case data seems good. Tech's comments say he cant find anything wrong with the case | No | RLN2MA/MY26B015996 | fexa | FEXA | False Alarm | RLN2MA | 50
2026-06-02 10:04 | WO-0583040 | Dollar General #20440 | 2026-05-19 | Door frame heater | Door heater plug was not fully plugged in | No | RLN3MA/MY26B016036 |  | FEXA | Doors | RLN3MA | 14
2026-06-02 10:03 | WO-0583039 | Dollar General #21709 | 2026-05-27 | False Alarm | Store connect cancelled this dispatch | Yes | RLN2MA/MY26B016465 |  | STORE CONNECT | False Alarm | RLN2MA | 6
2026-06-10 | WO-0588157 | Dollar General # 13069 | 2026-04-15 | Door not closed (Overnight) | Worked perfectly fine until the door never got closed on Jun 9th. Door Closed on jun 10th and its working fine after that | No | RMN4MA/MY26B014985 |  | STORE CONNECT | Doors | RMN4MA | 56
2026-06-09 09:29 | WO-0587865 | Dollar General #14341 | 2026-04-20 | Wrong / Loose wiring | No power to hot gas defrost solenoid. Tech fixed it and everything worked fine | Yes | RLN3MA/MY26B016495 |  | STORE CONNECT | Wrong / Loose wiring | RLN3MA | 50
2026-06-09 04:30 | WO-0587673 | Dollar General #22799 | 2026-03-18 | Door frame heater | Tech notes: Found case lights wired into the door heater controller fixed wiring and got lights on and door hearts wired correctly | No | RLN3MA/MY26B016006 |  | STORE CONNECT | Doors | RLN3MA | 83
#NAME?
2026-06-08 10:11 | WO-0586308 | Dollar General #20654 | 2026-03-25 | Door Gasket | Notes mentioned a new gasket is needed. | No | RLN2MA/MY26B016474 |  | STORE CONNECT | Doors | RLN2MA | 75
2026-06-08 08:03 | WO-0586957 | Dollar General #20761 | 2026-03-25 | False Alarm | Tech says he observed low ref. operation condition. But this MT case has been pulling down to temp before tech got there and the compressor is also cycling. | No | RMN4MA/MY26B016036 | fexa | STORE CONNECT | False Alarm | RMN4MA | 75
2026-06-13 08:13 | WO-0590801 | Dollar General #13396 | 2026-04-29 | High Store RH | Store connect dispatched this. Store was running high ambient then. No more such dispatches will happen until store ambient is fixed. | No | RLN2MA/MY26B016003 |  | STORE CONNECT | High Store RH | RLN2MA | 45
2026-06-12 10:51 | WO-0590856 | Dollar General #22286 | 2026-03-18 | False Alarm | Cant see any issue with this. Defrost seems fine, case seems to be pulling down. All tech did was force a defrost and left. Everything running exactly how it did before. | No | RMN4MA/MY26B016036 | fexa | STORE CONNECT | False Alarm | RMN4MA | 86
2026-06-12 09:21 | WO-0589971 | Dollar General #11509 | 2026-05-19 | Installation issue | All cases freedom and MD lost communication from Jun 10 4pm to jun 13 1pm | No | MY26B016494, RMN4MA/MY26B016536 |  | STORE CONNECT | Installation issue | RMN4MA | 24
2026-06-12 07:50 | WO-0589876 | Dollar General #22982 | 2026-04-14 | Installation issue | All freedom/MB cases in store are disconnected | No | RLN3MA/MY26B016502, MY26B016013, RLN4MA/MY26B014967 |  | RPM/SUZANNE B. | Installation issue | RLN3MA | 59
2026-06-12 06:48 | WO-0590766 | Dollar General #21778 | 2026-05-06 | Drain tube blocked | Has been getting good defrost for sure. Case temp is good too. No info from tech. Only thing I can think of that can cause water leak is blocked drain tube | No | RLN3MA/MY26D028107 |  | FEXA | Drain tube blocked | RLN3MA | 37
2026-06-12 06:35 | WO-0589851 | Dollar General #22281 | 2026-04-06 | Communication problem | Comm loss. All cases lost connection at the same time on all cases | No | RLN2MA/MY26C019876, MY26B016513, MY26B16019 |  | FEXA | Communication problem | RLN2MA | 67
2026-06-11 09:03 | WO-0588967 | Dollar General #22286 | 2026-03-18 | Door Torque | Eng sent this. Tech didn’t do any air leak testing which is why he was sent in the first place. He adjusted the defrost time but I have seen 45min defrost on this case from before he came in. There are some remote defrost changes done from pulse on jun 3. I'll check with Chris tomorrow. | No | RLN2MA/MY26B014938 |  | FEXA | Doors | RLN2MA | 85
2026-06-11 01:15 | WO-5089345 | Dollar General #16435 | 2026-03-25 | Installation issue | All cases (Freedom/Microblock) had power loss starting April 1st. Tech was able to get the power back on for the microblock cases but freedom still does not show any data. Tech's comments were that DG should have their contractors come take a look at the electrical | No | RMN4MA/MY26B013841 |  | FEXA | Installation issue | RMN4MA | 78
2026-06-11 | WO-0589359 | Dollar General #21135 | 2026-03-25 | Door Torque | Tech had to adjust door torque on 3 doors MT Case. The drain pan was full of water (probably because of excessive humidity into the case). The compressor discharge seems to be steady from the beginning. Don’t see any issues | No | RMN3MA/MY26B016480 |  | STORE CONNECT | Doors | RMN3MA | 78
2026-06-10 | WO-0588762 | Dollar General #14104 | 2026-03-24 | Door Gasket | Data looks okay. Pulling down to -10 pretty much and defrost is about 32. Could be icing. Notes say improper door seal. Could be the door gasket. And they also say waiting for parts so may be new gaskets were ordered? | No | RLN2MA/MY26B015990 |  | FEXA | Doors | RLN2MA | 78
2026-06-27 03:33 | WO-0600724 | Dollar General #20100 | 2026-06-17 | Overstocking | A box was not letting the door to close. | Yes | RLN2MA MY26D029644 |  | STORE CONNECT | Overstocking | RLN2MA | 10
2026-06-26 10:21 | WO-0599879 | Dollar General #21359 | 2026-04-28 | High Store RH | Store ambient sensor disconnected. Cant get the actual store ambient but tech notes say store ambient is high. Let controls team know about it. | No | RLN3MA / MY26B016014 |  | STORE CONNECT | High Store RH | RLN3MA | 59
2026-06-26 10:00 | WO-0599854 | Dollar General #20440 | 2026-05-19 | Door Torque | Appears door was left open overnight. | No | RLN3MA/ MY26D032603 |  | FEXA | Doors | RLN3MA | 38
2026-06-26 10:00 | WO-0599854 | Dollar General #20440 | 2026-05-19 | Installation issue | Cases were not leveled at all per tech. They were leaning forward. Doors were also not sealing well. Could be door torque as well but cant confirm. | No | RLN3MA/ MY26D032603 |  | FEXA | Installation issue | RLN3MA | 38
2026-06-26 04:15 | WO-0600225 | Dollar General #10520 | 2026-06-26 | False Alarm | Tech says all the cases are meeting temps. | Yes | RLN3MA / MY26E039362 | sc | STORE CONNECT | False Alarm | RLN3MA | 0
2026-06-25 11:55 | WO-0599278 | Dollar General #13009 | 2026-05-27 | Door not closed (Overnight) | Data shows a sudden rise in temp and not getting back down. Door most likely did not close. The tech went ahead and recharged the cassette when that was not an issue here. Case pulled back down before he came in | No | RLN2MA / MY26C019875 |  | TIM SMITH | Doors | RLN2MA | 29
2026-06-25 07:29 | WO-0599624 | Dollar General #21838 | 2026-06-17 | False Alarm | Recalled the dispatch since the case was returning the normal | Yes | RMN4MA/MY26E039403 |  | FEXA | False Alarm | RMN4MA | 8
2026-06-25 03:38 | WO-0599522 | Dollar General #20597 | 2026-04-22 | Door Gasket | Door gasket got uninstalled on one door. | No | RLN3MA/MY26B016493 |  | FEXA | Doors | RLN3MA | 64
2026-06-24 04:43 | WO-0598739 | Dollar General #6987 | 2026-06-16 | False Alarm | FEXA flase alarm. Data shows the case is running perfectly fine | Yes | RMN4MA/MY26E039399 |  | TAVANT/BRANCH - RICHARD JOHNSON/INSTALLTION | False Alarm | RMN4MA | 8
2026-06-23 11:42 | WO-0597607 | Dollar General #21342 | 2026-04-10 | Unknown | Notes say major ice build up on doors and water on floor. Could be the door frame heater wiring issue | Yes | RLN3MA/MY26B016018 |  | STORE CONNECT | Unknown | RLN3MA | 74
2026-06-23 10:03 | WO-0597498 | Dollar General #22864 | 2026-03-24 | False Alarm | FEXA flase alarm. Data shows the case is running perfectly fine | No | RMN5MA/MY26B016552 |  | STORE CONNECT | False Alarm | RMN5MA | 91
2026-06-22 11:07 | WO-0596795 | Dollar General #20100 | 2026-06-17 | Door Torque | Tech noticed the doors not closing all by themselves. Adjusted the torque. Everything else seemed okay. | Yes | RMN4MA / MY26E039404 |  | STORE CONNECT | Doors | RMN4MA | 5
2026-06-19 11:18 | WO-0595748 | Dollar General #22286 | 2026-03-18 | Communication problem | Double defrost issue. | No | RLN2MA /MY26B014938 |  | STORE CONNECT | Communication problem | RLN2MA | 93
2026-06-18 10:28 | WO-0594944 | Dollar General #22286 | 2026-03-18 | Door not closed (Overnight) | From notes. It looks like the door was left open | No | RMN5MA/MY26B016552 |  | FEXA | Doors | RMN5MA | 92
2026-06-18 06:40 | WO-0594225 | Dollar General #14386 | 2026-06-15 | Component Failure | Cassette didn’t function correctly from the beginning. Cassette was returned. Don’t know the root cause yet | Yes | RLN2MA MY26B016452 |  | STORE CONNECT | Component Failure | RLN2MA | 3
2026-06-18 02:08 | WO-0594191 | Dollar General # 13070 | 2026-04-14 | Door not closed (Overnight) | Door was left open | No | RMN4MA/MY26B014986 |  | STORE CONNECT | Doors | RMN4MA | 65
2026-06-16 03:39 | WO-0593126 | Dollar General #22286 | 2026-03-18 | Communication problem | Double defrost issue. | No | RLN2MA MY26B014938 |  | FEXA | Communication problem | RLN2MA | 90
2026-06-16 02:19 | WO-0592610 | Dollar General #20761 | 2026-03-25 | Door not closed (Overnight) | Door not closed | No | RLN2MA MY26B013813 |  | STORE CONNECT | Doors | RLN2MA | 83
2026-06-15 10:50 | WO-0592045 | Dollar General #23988 | 2026-06-08 | Component Failure | HG valve not working | Yes | RLN2MA MY26C025304 |  | TIM SMITH | Component Failure | RLN2MA | 7
2026-06-15 10:44 | WO-0592039 | Dollar General #20107 | 2026-05-06 | Door not closed (Overnight) | Door not closed. | No | RMN3MA MY26C025312 |  | FEXA | Doors | RMN3MA | 40
2026-07-06 16:10 | WO-0608904 | Dollar General #20761 | 2026-03-25 | Door Torque | Appears to be a door opening issue. Alarm self-cleared | No | RLN2MA / MY26B013813 |  | STORE CONNECT | Doors | RLN2MA | 103
2026-07-06 15:23 | WO-0608855 | Dollar General #3277 | 2026-05-07 | Door Torque | Door torque. Tech repaired it Alarm lasted for 40 min before self-clearing | No | RLN3MA / MY26D028108 |  | TIM SMITH | Doors | RLN3MA | 60
2026-07-06 11:48 | WO-0608593 | Dollar General #1768 | 2026-05-13 | High Store RH | RH is over 60% for over 16hours | No | RLN2MA / MY26D028097 |  | FEXA | High Store RH | RLN2MA | 54
2026-07-06 08:28 | WO-0608327 | Dollar General #21606 | 2026-03-03 | Door not closed (Overnight) | Appears door was left open overnight. WO canceled | No | RLN3MA / MY26B013826 |  | STORE CONNECT | Doors | RLN3MA | 125
2026-07-03 22:52 | WO-0607313 | Dollar General #21375 | 2026-03-10 | Door not closed (Overnight) | Appears door was left open overnight. | No | RLN3MA / MY26B01382 |  | FEXA | Doors | RLN3MA | 115
2026-07-03 22:38 | WO-0607311 | Dollar General #22930 | 2026-04-16 | Unknown | Water leaking. Don’t know why, everything seems | Yes | RLN4MA / MY26B014974 |  | FEXA | Unknown | RLN4MA | 78
2026-07-03 14:40 | WO-0607008 | Dollar General #21838 | 2026-06-17 | Door not closed (Overnight) | Door not closed overnight | Yes | RLN3MA / MY26E039365 |  | STORE CONNECT | Doors | RLN3MA | 16
2026-07-03 00:52 | WO-0606554 | Dollar General #14858 | 2026-03-16 | Unknown | Case running high superheat. Will keep monitoring it for the root cause | Yes | RLN2MA / MY26B016475 |  | STORE CONNECT | Unknown | RLN2MA | 109
2026-07-03 | WO-0607304 | Dollar General #22408 | 2026-06-30 | Door Torsion rod | Nothing wrong with case performance. All sensors were reading correct. Tech found a bad torque rod. The only case not making temp is a RFLN4 | Yes | RMN5MA/MY26E03940 |  | FEXA | Doors | RMN5MA | 3
2026-07-02 22:04 | WO-0606498 | Dollar General #8773 | 2026-04-13 | False Alarm | Incident was caused by heavy shopping. WO was canceled | No | RLN3MA / MY26B016492 |  | STORE CONNECT | False Alarm | RLN3MA | 80
2026-07-02 | WO-0605720 | Dollar General #21664 | 2026-06-30 | Unknown | Unknown. Left unit is running at ~50° Dispatch was rejected for Dallas branch | Yes | RMN5MA / MY26D033044 |  | FEXA | Unknown | RMN5MA | 2
2026-07-02 | WO-0606044 | Dollar General #21938 | 2026-07-01 | Communication problem | RH Sensor (One connect box) | Yes |  |  | STORE CONNECT | Communication problem |  | 1
2026-07-02 | WO-0605513 | Dollar General #22408 | 2026-06-30 | Wrong / Loose wiring | Tech found wiring issue on the MB. Does not say what is wrong but notes say he fixed it and case is pulled down fine after | Yes | RLN3MA / MY26F047534 |  | STORE CONNECT | Wrong / Loose wiring | RLN3MA | 2
2026-06-30 | WO-0603741 | Dollar General #20597 | 2026-04-22 | Door not closed (Overnight) | Left the door open. Had defrost after 3hrs of door opening. Further increased the alarm turn on time. Had to dispatch. Door remained open for 7hours | No | RLN3MA / MY26B016493 |  | FEXA | Doors | RLN3MA | 69
2026-06-30 | WO-0603718 | Dollar General #13069 | 2026-04-15 | High Store RH | High temp alarm self cleared. | No | RLN3MA / MY26B016491 |  | STORE CONNECT | High Store RH | RLN3MA | 76
2026-06-30 | WO-0602689 | Dollar General #20440 | 2026-05-19 | Door frame heater | Frame heater for doors not wired correctly | No | RLN3MA / MY26D032603 |  | FEXA | Doors | RLN3MA | 42
2026-06-29 | WO-0601570 | Dollar General #22149 | 2026-03-11 | Door not closed (Overnight) | Door not closed overnight | No | RLN2MA / MY26B014945 |  | FEXA | Doors | RLN2MA | 110
2026-07-09 21:39 | WO-0611639 | Dollar General #21257 | 2026-07-08 | Wrong program | LT unit had MT program from the beginning. | No | RLN3MA / MY26F047544 |  | TIM SMITH | Wrong program | RLN3MA | 1
2026-07-08 21:05 | WO-0610829 | Dollar General #21778 | 2026-05-06 | Drain tube blocked | Issue with drain line leaking into case | No | RLN3MA / MY26D028107 |  | FEXA | Drain tube blocked | RLN3MA | 63
2026-07-08 19:55 | WO-0610807 | Dollar General #8773 | 2026-04-13 | Unknown | Unknown cause. Will need to wait for tech's notes | Yes | RLN3MA / MY26B016492 |  | FEXA | Unknown | RLN3MA | 86
2026-07-08 02:18 | WO-0609997 | Dollar General #13009 | 2026-05-27 | Door Torque | Case started pulling back down after door was closed. but on July 9th, tech shut case off for 11min, I don't know what the service tech did on the last one. They stated the added R-290 to restore proper charge. The case was not shut down long enough to pull a vacuum and recharge the system. I'm assuming they added charge to increase the suction pressure where they thought it should be. The case is no longer meeting temperature. | No | RLN2MA / MY26C019875 |  | FEXA | Doors | RLN2MA | 42
#NAME?
2026-07-14 13:55 | WO-0614619 | Dollar General #10339 | 2026-04-29 | Door Gasket | Updated notes. Moved from unknown to door gasket based on updated tech notes. Unable to determine the source of this leak from one connect | No | RLN3MA / MY26C025307 |  | FEXA | Doors | RLN3MA | 76
2026-07-13 16:59 | WO-0614010 | Dollar General #10095 | 2026-07-12 | Installation issue | Sensors unplugged from controller during install. Got 15min data then got disconnected | Yes | RMN3MA/MY26D026813 |  | FEXA | Installation issue | RMN3MA | 1
2026-07-13 16:33 | WO-0613989 | Dollar General #12959 | 2026-07-08 | High Store RH | Store ambient was 113F | Yes | RLN2MA/MY26E034934 |  | FEXA | High Store RH | RLN2MA | 5
2026-07-13 13:20 | WO-0613796 | Dollar General #20021 | 2026-06-10 | Door - general | Door hold open was broken | Yes | RMN3MA / MY26C025322 |  | FEXA | Doors | RMN3MA | 33
2026-07-13 11:08 | WO-0613652 | Dollar General #22425 |  | False Alarm | Call was placed during the install. Case was not connected to SC | No | RLN3MA / MY26F047552 |  | STORE CONNECT | False Alarm | RLN3MA
2026-07-13 03:31 | WO-0613360 | Dollar General #21742 | 2026-06-16 | High Store RH | Store ambient went upto 90F | Yes | RLN3MA / MY26E034942 |  | FEXA | High Store RH | RLN3MA | 27
2026-07-12 04:40 | WO-0612961 | Dollar General #12377 | 2026-07-08 | Door not closed (Overnight) | Door was left open overnight. Tech mentioned that door torque actually fixed the issue | Yes | RMN4MA / MY26D028118 |  | STORE CONNECT | Doors | RMN4MA | 4
2026-07-12 01:09 | WO-0612947 | Dollar General #3359 |  | High Store RH | Store ambient went upto 95F | No | RLN3MA / MY26B016010 |  | STORE CONNECT/FEXA | High Store RH | RLN3MA
2026-07-11 21:37 | WO-0612914 | Dolalr General #22040 |  | Ref. leak/ Low charge | Case had higher discharge air temp. Tech recharged the case and it started pulling down | No | RMN4MA / MY26F048133 |  | FEXA | Ref. leak/ Low charge | RMN4MA
2026-07-11 21:12 | WO-0612908 | Dollar General #21742 | 2026-06-16 | High Store RH | Store ambient going upto 90F | Yes | RLN3MA / MY26E034942 |  | STORE CONNECT | High Store RH | RLN3MA | 25
2026-07-11 19:14 | WO-0612878 | Dollar General #21548 |  | Ref. leak/ Low charge | Case had higher discharge air temp. Tech recharged the case and it started pulling down | No |  |  | FEXA | Ref. leak/ Low charge
2026-07-11 14:24 | WO-0612734 | Dollar General #10520 | 2026-06-26 | Overstocking | Overstocking the product prevented the door from closing all the way | Yes | RLN3MA / MY26E039362 |  | FEXA | Overstocking | RLN3MA | 15
2026-07-11 08:48 | WO-0612539 | Dollar General #22086 | 2026-06-22 | False Alarm | FEXA called about case temp reading 61degrees. The SC data doesn’t show that. | Yes | RLN3MA MY26E039361 |  | FEXA | False Alarm | RLN3MA | 19
2026-07-10 15:59 | WO-0612255 | Dollar General #10520 | 2026-06-26 | Overstocking | High temp alarm. Overstocking the case prevented the door from closing. | Yes | RLN3MA / MY26E039362 |  | STORE CONNECT | Overstocking | RLN3MA | 14
2026-07-10 14:04 | WO-0612151 | Dollar General #12377 | 2026-07-08 | High Store RH | Store ambient reaching 93F | Yes | RMN4MA / MY26F048132 |  | STORE CONNECT | High Store RH | RMN4MA | 2
2026-07-10 10:02 | WO-0611903 | Dollar General #2606 | 2026-07-06 | Drain tube blocked | Drain tube was leaking into the case | No | RMN3MA / MY26E039395 |  | STORE CONNECT | Drain tube blocked | RMN3MA | 4
2026-07-20 | WO-0618533 | Dollar General #20336 | 2026-04-14 | Door frame heater | Door frame heater was wired incorrectly. The RH in store is above 65% |  | RLN3MA / MY26B016487 |  | STORE CONNECT | Doors | RLN3MA | 97
2026-07-19 | WO-0618250 | Dollar General #4608 | 2026-06-30 | Drain tube blocked | Water leaking from top of the case into the cooler. Could be a block drain? | No | RMN5MA / MY26E039407 |  | STORE CONNECT | Drain tube blocked | RMN5MA | 19
2026-07-18 12:15 | WO-0617620 | Dollar General #22613 | 2026-03-18 | Drain tube blocked | Water leaking from top of the case into the cooler. Could be a block drain? | No | RLN3MA / MY26B016009 |  | INTERNAL | Drain tube blocked | RLN3MA | 122
2026-07-17 21:18 | WO-0617378 | Dollar General #22247 | 2026-07-16 | Door - general | Door hinge plate mounting bolts are rubbing against the door. | Yes | RMN4MA / MY26F048122 |  | STORE CONNECT | Doors | RMN4MA | 1
2026-07-17 06:33 | WO-0616082 | Dollar General #21404 | 2026-07-15 | Installation issue | This is a ref. leak issue but copper tube near filter drier cracked. The way the tube is right now, it could not have been shipped that way because it cant be boxed. Something happened during the installation? | Yes | RMN3MA / MY26C025178 |  | FEXA | Installation issue | RMN3MA | 2
2026-07-16 17:52 | WO-0616509 | Dollar General #3277 | 2026-05-07 | False Alarm | Wrong serial entered. This case has no issues. WO-0615761 was the actual issue | No | RLN3MA / MY26d028108 MY26B015987 |  | FEXA | False Alarm | RLN3MA | 70
2026-07-15 21:43 | WO-0615761 | Dollar General #3277 | 2026-05-07 | Door Gasket | Center door gasket pulled loose. Same case had issues in WO-0608855 | No | RLN3MA / MY26D028108 |  | STORE CONNECT | Doors | RLN3MA | 69
2026-07-15 11:21 | WO-0615276 | Dollar General #20021 | 2026-06-10 | Freedom | Tech fixed a case with water pump issues. Must be a freedom case. | Yes | RMN4MA / MY26E038206 |  | STORE CONNECT/FEXA | Freedom | RMN4MA | 35
2026-07-14 15:30 | WO-0614727 | Dollar General #13009 | 2026-05-27 | Communication problem | Display was showing "----". This was a problem observed initially on the controllers. Vinod looking into this | No | RLN2MA / MY26C019875 |  | STORE CONNECT | Communication problem | RLN2MA | 48
#NAME?
#NAME?
#NAME?
#NAME?
#NAME?
#NAME?
#NAME?
#NAME?
#NAME?
#NAME?
#NAME?
#NAME?
#NAME?
#NAME?
#NAME?
#NAME?
#NAME?
#NAME?
#NAME?
#NAME?
#NAME?
#NAME?
#NAME?
#NAME?
#NAME?
#NAME?
#NAME?
#NAME?
#NAME?
#NAME?
#NAME?
#NAME?
#NAME?
#NAME?
#NAME?
#NAME?
#NAME?
#NAME?
#NAME?
#NAME?
#NAME?
#NAME?
#NAME?
#NAME?
#NAME?
#NAME?
#NAME?
#NAME?
#NAME?
#NAME?
#NAME?
#NAME?
#NAME?
#NAME?
#NAME?
#NAME?
#NAME?
#NAME?
#NAME?
#NAME?
#NAME?
#NAME?
#NAME?
#NAME?
#NAME?
#NAME?
#NAME?
#NAME?
#NAME?
#NAME?
#NAME?
#NAME?
Formulas:
Call Date = IFERROR(INDEX('Raw Data'!$D3:D398,MATCH([Work Order],'Raw Data'!$H3:H398,0)),"")
Commission Date = IFERROR(INDEX('Store List'!$B4:B300,MATCH([Store],'Store List'!$A4:A300,0)),"")

## Sheet1 (hidden)
Temp | 0 hrs | 1st hr | 2nd hrs | 3rd hour | 4th hour | 5th hour
3 | wait | Internal cntrl alarm | no action |  | alert 0 to 1 | dispatch
|  |  | 7200 sec start |  | triage | can be recalled before 7am

## Raw Data
Possible duplicate work orders: |  | 4
(Do Not Modify) WO Number | (Do Not Modify) Row Checksum | (Do Not Modify) Modified On | DATE | APRILS NOTES | STATUS | COMPLETED DATE | BOS WORK ORDER | BRANCH | STORE | CITY | STATE | PO | CALLER | PROBLEM CATEGORY | REPLACEMENT PARTS | NON-WARRANTY BILLABLE | FR SUBMITTED YES/NO | CASE MODEL/SERIAL NUMBER | PICTURES BOS | Job Scope | WORK SUMMARY
|  |  | 2026-07-06 16:10 |  | Canceled | 2026-07-06 | WO-0608904 | San Antonio, TX | Dollar General #20761 | Pettus | TX | TAVANT/PRODUCT CARE | STORE CONNECT | TEMPERATURE |  |  |  | RLN2MA / MY26B013813 |  | High Temperature Alarm | Product Care Team cancelled the call
|  |  | 2026-07-06 15:23 |  | Completed | 2026-07-07 | WO-0608855 | Dallas, TX | Dollar General #3277 | Garland | TX | 5169188 | FEXA | TEMPERATURE |  |  |  | RLN3MA / MY26D028108 |  | Invalid Temperature Reading | I found case at temp -8 down to - 10 i found left hand door not closing all the way and probably causing issues store had roped off the case i repaired torque rod and adjusted it . No other issues found with the case. Store ac is not working properly could case issues not sure.
|  |  | 2026-07-06 11:48 | ETA 7/6 | Scheduled |  | WO-0608593 | Kansas City, MO (Lenexa) | Dollar General #1768 | Nixa | MO | 5163557 | FEXA | WATER LEAKING |  |  |  | RLN2MA / MY26D028097 |  | Water leaking from under the unit and excessive condinsation on the doors - multiple units effected
|  |  | 2026-07-06 08:28 |  | Canceled |  | WO-0608327 | Tulsa, OK | Dollar General #21606 | Porum | OK | TAVANT/PRODUCT CARE | STORE CONNECT | TEMPERATURE |  |  |  | RLN3MA / MY26B013826 |  | High Temperature Alarm | Kindly recall the dispatch for below case, as case trends and working seems to be normal, kindly acknowledge here once it is recalled.
|  |  | 2026-07-03 22:52 |  | Completed | 2026-07-07 | WO-0607313 | Southern | Dollar General #21375 | Oxford | AR | 5162624 | FEXA | ICE BUILD UP |  |  |  | RLN3MA / MY26B01382 |  | There is a block of ice on the inside and top of the unit | Email from Young, Bradley <Bradley.Young@hussmann.onmicrosoft.com>
|  |  | 2026-07-03 22:38 | ETA 7/8 | Scheduled |  | WO-0607311 | Dallas, TX | Dollar General #22930 | Forestburg | TX | 5162381 | FEXA | WATER LEAKING INTO UNIT |  |  |  | RLN4MA / MY26B014974 |  | There is water running into the unit and down the shelves and freezing
|  |  | 2026-07-03 14:40 |  | Completed |  | WO-0607008 | Southern | Dollar General #21838 | Belle Chasse | LA | TAVANT/PRODUCT CARE | STORE CONNECT | TEMPERATURE |  |  |  | RLN3MA / MY26E039365 |  | High Temperature Alarm | Found ice dripping from top of cabinet. Checked to make sure the drain was clear. Removed top plate to inspect where water was coming from. Found spray foam and butyl had overflowed into airway and had ice forming on it and wicking water down to cabinet. Removed overflow and all ice. Observed for 45 minutes to ensure it didn't continue leaking. Observed defrost and proper drain function.
|  |  | 2026-07-03 00:52 | Pinged Sarah for eta | Send New Tech |  | WO-0606554 | Houston, TX | Dollar General #14858 | Houston | TX | TAVANT/PRODUCT CARE | STORE CONNECT | TEMPERATURE |  |  |  | RLN2MA / MY26B016475 |  | High Temperature Alarm
|  |  | 2026-07-03 | Parts ordered and tech returning with propane | Done - Send New Tech |  | WO-0607304 | Houston, TX | Dollar General #22408 | Angelton | TX | 5162382 | FEXA | TEMPERATURE |  |  |  | RMN5MA/MY26E03940 |  | Invalid Temperature Reading | 7/7/2026 .Tech support called me after I left. 7/7/2026 One of the units might be under charged so they asked me to go back with some propaneChecked in with manager. Located 5 door case. Found unit at temp. Connected to both controllers. Found all sensors reading properly. Tried to get with tech support but couldnt get a hold of them. Found 1 torque rod and master that need to repaced. Got with andrew miller we checked all sensors . Will return when parts come in
|  |  | 2026-07-02 22:04 |  | Canceled | 2026-07-03 | WO-0606498 | Bolingbrook, IL | Dollar General #8773 | South Bend | IN | TAVANT/PRODUCT CARE | STORE CONNECT | TEMPERATURE |  |  |  | RLN3MA / MY26B016492 |  | High Temperature Alarm | 7/3/2026 2:02AM Please recall the dispatch request, as the case has started returning to normal. Regards,Product Care Team
|  |  | 2026-07-02 |  | Completed | 2026-07-07 | WO-0605720 | Dallas, TX | Dollar General #21664 | Jacksonville | TX | TAVANT/PRODUCT CARE | STORE CONNECT | TEMPERATURE |  |  |  | RMN5MA / MY26D033044 |  | High Temperature Alarm | 07/02/26; Check new cases and found the new case, SN MY26D033044 warm in the left end. Case has two condensing units. Pull inside top cover to access the evap, evap clear. Condensing units are R290. Discharge temp feels low at the condenser inlet. Leak check unit, found no leaks. Will have to pick up an R290 charging kit and return. Spoke with the manager about it and they are fine. 07/06/26; Pick up R290 kit in Longview and return to the store. Install piercing valveson liquid and suction. Hookup hoses and vacuum pump, vacuum pump locked up. Pick up new vacuum pump. 07/07/26; Return to store. Activate piercing valves and pull vacuum. Leave unit on vacuum for an hour, vacuum stayed at 30". Weigh in 3.5 oz of R290. Discharge temp at condenser is at 110°F. Suction at 50# and discharge at 140#. Case temp droped to setpoint and cycled.
|  |  | 2026-07-02 | ETA is 7/17 | Return Needed |  | WO-0606044 | Denver, CO | Dollar General #21938 | Olathe | CO | TAVANT/Tim Smith (Installation) | INTERNAL | HUMIDITY SENSOR | [6 empty] | 07/02/26; Check new cases and found the new case, SN MY26D033044 warm in the left end. Case has two condensing units. Pull inside top cover to access the evap, evap clear. Condensing units are R290. Discharge temp feels low at the condenser inlet. Leak check unit, found no leaks. Will have to pick up an R290 charging kit and return. Spoke with the manager about it and they are fine. 07/06/26; Pick up R290 kit in Longview and return to the store. Install piercing valveson liquid and suction. Hookup hoses and vacuum pump, vacuum pump locked up. Pick up new vacuum pump. 07/07/26; Return to store. Activate piercing valves and pull vacuum. Leave unit on vacuum for an hour, vacuum stayed at 30". Weigh in 3.5 oz of R290. Discharge temp at condenser is at 110°F. Suction at 50# and discharge at 140#. Case temp droped to setpoint and cycled.
|  |  | 2026-07-02 |  | Completed | 2026-07-02 | WO-0605513 | Houston, TX | Dollar General #22408 | Angleton | TX | TAVANT/PRODUCT CARE | STORE CONNECT | TEMPERATURE |  |  |  | RLN3MA / MY26F047534 |  | High Temperature Alarm | Checked in with manager. Located self contained unit. Found unit at -4 degrees. Right side condenser was not running. Connected to controller. Controller was calling for comp. Started going thru control wiring. Found a wiring issue. Repaired wiring. Started condenser up. Unit dropped to temp. Checked operation of unit. All okay work complete
|  |  | 2026-06-30 |  | Completed | 2026-07-02 | WO-0603741 | Bolingbrook, IL | Dollar General #20597 | Chicago | IL | TAVANT/PRODUCT CARE | STORE CONNECT | TEMPERATURE |  |  |  | RLN3MA / MY26B016493 |  | High Temperature Alarm | 7/1/26 DE Arrived on site and checked in. On site for reach in freezer running warm. Case controllers were reading -8 and -4 upn arrival. Case went into defrost immediately after arrival. Let case run through its natural defrost cycle. After defrost, let case try to pull down to temp. Customers kept opening doors so case was struggling to pull down to temp. Doors were finally left closed long enough for case to pull down. Case temping at -.5 and .1 and still dropping upon departure. No issue found at this time. Cleaned up work area and checked out with manager Sylvia.
|  |  | 2026-06-30 |  | Canceled | 2026-07-01 | WO-0603718 | Southern | Dollar General #13069 | Laurel | MS | TAVANT/PRODUCT CARE | STORE CONNECT | TEMPERATURE |  |  |  | RLN3MA / MY26B016491 |  | High Temperature Alarm | 7/1 Kindly recall the dispatch for below case, as case trends and working seems to be normal, kindly acknowledge here once it is recalled. From Product Care 6/30 Roll call for AM as store closes in 35 minutes
|  |  | 2026-06-30 |  | Completed | 2026-06-30 | WO-0602689 | Houston, TX | Dollar General #20440 | Sheridan | TX | TAVANT/PRODUCT CARE | STORE CONNECT | TEMPERATURE |  |  |  | RLN3MA / MY26D032603 |  | High Temperature Alarm | 7/1 checked in with manager . Located rif self contained unit. Found unit at 18 degrees. Found ice build up on frame of case not allowing doors to close properly. Removed ice from frame , case started dropping to temp. Started looking into frame heater. Located anti sweat contoller in top left panel of case. Found good voltage coming in and out of contoller. Started tracing wiring for frame heater. Had to go wire for wire to locate frame heater. Found that frame heater wasnt wired properly. Fixed wiring. Frame heater started pulling correct amps , ice melted off frame. Checked operation of unit. Units are charged properly. Tried to check deforst but controllers were locked out. Had to get with tech support to download the correct app for carel controllers. Tested defrost. Had to install a self tapper on condenser because ribbits had come loose . All okay. Work complete
|  |  | 2026-06-29 | Pinged Heidi - ETA was 7/6 | Unscheduled |  | WO-0601570 | Tulsa, OK | Dollar General #22149 | Anton | TX | TAVANT/PRODUCT CARE | STORE CONNECT | TEMPERATURE |  |  |  | RLN2MA / MY26B014945 |  | High Temperature Alarm
|  |  | 2026-06-27 03:33 |  | Completed | 2026-06-27 | WO-0600724 | Southern | Dollar General #20100 | Paulina | LA | TAVANT/PRODUCT CARE | STORE CONNECT | TEMPERATURE |  |  |  | RLN2MA MY26D029644 |  | High Temperature Alarm | Checked case and found that the evaporator coil was iced up and it was because there was a box of product that was keeping the door open, so after moving the box and closing the door i had to run the case in multiple defrost. After that case came back down yo temperature and its now running normally.
|  |  | 2026-06-26 10:21 |  | Send New Tech |  | WO-0599879 | Houston, TX | Dollar General #21359 | Orange | TX | 5134984 | FEXA | TEMPERATURE |  |  |  | RLN3MA / MY26B016014 |  | Ice cream is melting and product damaged, water leaking under unit | 6/26/26 Freezer iced up due to high humidity in area.customer removed all product then i deiced case.defrost heaters working properly.i also cleaned drain pan assembly.also cleaned condenser coils.then put unit it online.frerzer maintaining temperature -8 degrees
|  |  | 2026-06-26 10:00 |  | Completed | 2026-06-27 | WO-0599854 | Houston, TX | Dollar General #20440 | Sheridan | TX | 5140629 | FEXA | TEMPERATURE |  |  |  | RLN3MA/ MY26D032603 |  | Cooler keeps freezing up, causing door to form ice and it is not closing | 6/26/26 Arrived on site checked in with manager. Found 3 door case with some ice building up at bottom of door. Removed ice pulled gaskets and set outside in the sun to warm up. Reinstalled and adjusted torque rods on Doors. Doors seem to be Sealing better and can not feel any air leaks. After talking to non-mechanical technician cases may not be leveled correctly. Checked with makeshift plumber Bob and cases seem to be leaning forward. Non-mechanical technicians or installing contractor may need to check level on cases. Cases are out of alarm at this time. Checked out with store m o d work order complete.
|  |  | 2026-06-26 04:15 |  | Completed | 2026-06-27 | WO-0600225 | Southern | Dollar General #10520 | Youngsville | LA | TAVANT/PRODUCT CARE | STORE CONNECT | TEMPERATURE |  |  |  | RLN3MA / MY26E039362 |  | High Temperature Alarm | 6/27/26 Service call for frozen food micro blocks high temp. Drove to site, checked in, gained access to cases, all 3 micro blocks are working as they should with no alarm, and cases are at setpoint. Serial: MY26D029643 MODEL ID: RLN2MA MODEL ID: RLN3MA SERIAL: MY26E039362
|  |  | 2026-06-25 11:55 |  | Completed | 2026-06-26 | WO-0599278 | Southern | Dollar General #13009 | Wake Village | TX | TAVANT/PRODUCT CARE | STORE CONNECT | TEMPERATURE |  |  |  | RLN2MA / MY26C019875 |  | High Temperature Alarm | 6/26/26 Arrived onsite to service Hussmann reach-in case. Recovered the existing R-290 refrigerant charge, pulled the system into a deep vacuum, and recharged the system with 3.5 oz of R-290. Restarted the unit and verified proper operation. Case temperature is currently -7°F and maintaining temperature as designed. Unit operating normally at this time. 6/25/26- inspected the system. Checked the airflow. Checked that the compressor was running. Determined that the system was low on R290. Will have Dave return tomorrow to gas up the system.
|  |  | 2026-06-25 07:29 |  | Completed | 2026-06-26 | WO-0599624 | Southern | Dollar General #21838 | Belle Chasse | LA | TAVANT/PRODUCT CARE | STORE CONNECT | TEMPERATURE |  |  |  | RMN4MA/MY26E039403 |  | High Temperature Alarm | 6/26 Please recall the dispatch requst, as the case has started returning to normal. Regards, Product Care Team 6/25When i got to site i found the evaporator was iced up because the vendor had the doors open as he was installing sliders and fillling it with product, So i tested defrost out and its working normally the case will recover when they are done loading the case
|  |  | 2026-06-25 03:38 |  | Completed | 2026-06-25 | WO-0599522 | Bolingbrook, IL | Dollar General #20597 | Chicago | IL | TAVANT/PRODUCT CARE | STORE CONNECT | COIL ICING |  |  |  | RLN3MA/MY26B016493 |  | We are observing a coil icing | 6/25/26 AN Model# RLN3MA Serial# MY26B016493 Drove to site. Arrived on site. Call for frozen 3 door icing up. Found right most door had gasket off at the bottom of the door keeping door open causing moisture to enter into case. Ice was forming on ceiling of case. Reinstalled gasket. Cleared ice forming on door frame. Door is now closing proper. Forced both controllers through multiple defrosts to clear any frost from coils. Cleared as much ice and moisture as possible. Monitored temps. Temps are dropping. At 0 degrees and still dropping. Cleaned up work area. Work complete
|  |  | 2026-06-24 04:43 |  | Completed | 2026-06-25 | WO-0598739 | RPM/Strategic Accounts | Dollar General #6987 | Pinetop | AZ | 5129550 | FEXA | TEMPERATURE |  |  |  | RMN4MA/MY26E039399 |  | I spoke with Marie (SM) and she said temperature seemed warm and product didn't look good and the temperature gauge was not working. | Sub sending in tech notes
|  |  | 2026-06-23 11:42 |  | Completed | 2026-06-26 | WO-0597607 | RPM/Strategic Accounts | Dollar General #21342 | Klamath Falls | OR | 5130014 | FEXA | ICE BUILD UP |  |  |  | RLN3MA/MY26B016018 |  | Major Ice build up on the doors and leaking water on floor | Sub confirms complete and will send in tech notes
|  |  | 2026-06-23 10:03 |  | Completed | 2026-06-23 | WO-0597498 | Phoenix, AZ | Dollar General #22864 | Tucson | AZ | 5119317 | FEXA | TEMPERATURE |  |  |  | RMN5MA/MY26B016552 |  | Not Keeping Temperature | Arrived on site and checked in with mod. Cooler reach in at temp upon arrival. Pulled product and panels. Coil free and clear of ice. Fans working. Compressor running. Condenser fan running and clear of dust and debris. Solenoid operational. Superheat ok. Dixell controller working. Correct amount of defrost and defrost time set. Changed high temp alarm from 47° to 65°. Job complete
|  |  | 2026-06-22 11:07 |  | Completed | 2026-06-22 | WO-0596795 | Southern | Dollar General #20100 | Paulina | LA | TAVANT/PRODUCT CARE | STORE CONNECT | TEMPERATURE |  |  |  | RMN4MA / MY26E039404 |  | High Temperature alarm | On arrival case was not temping high, checked airflow and confirmed it was good, checked condensing unit and cleaned the small layer of dust I noticed. Also tensioned doors after noticing they do not close by themselves after opening.
|  |  | 2026-06-19 11:18 | Scheduled for 6/26 return (DG Manager requested return to check on it) | Return Needed |  | WO-0595748 | Phoenix, AZ | Dollar General #22286 | Arizona City | AZ | 5123730 | FEXA |  |  |  |  | RLN2MA /MY26B014938 |  | Not Working at All - Temp is failing, Ice Cream Melting, Product Damaged | Arrived at store checked in with manager checked 2dr freezer and case was running at -6°F talked to manager amd he dont like how temp spikes up 6-8°af after opening door for 10-15 sec case dropps to temp after door closes. Called tech support and spoke with Erik we went through all perameters and chexked temp graph we did find the case is going into 2 defroat back to back. Erik ssaid it ahould be a program issue and that they coulsld do the changes remotely. Case was running at -7° when i left store.
|  |  | 2026-06-18 10:28 |  | Completed | 2026-06-19 | WO-0594944 | Phoenix, AZ | Dollar General #22286 | Arizona City | AZ | 5125380 | FEXA | TEMPERATURE |  |  |  | RMN5MA/MY26B016552 |  | High temperature alarm | 6/19 Arrived at store checked in with manager looked for case mentioned on work summary RMN5MA MY26B016552 and there is no case in store with this model# and serial#. Store did have a issue with a 2dr freezer manager said case was to warm during defrost and temp got upto 48°F and took a long time to drop. Case was running at -9°F when i arrived. Checked defrost perameters and found it was programmed for defroat interval of 6hrs changed that to every 8hrs also found max defrost duration set to 60 min changed that to 25 min also end defrost temp was set to 45° changed that to 36°F after making changes ran system throu a defrost cycle ansd monitored case temp did not go higher then 36°F and after defrost case dropped temp case is running at -5°F when i left store. No other issues present at time of departure Arrived onsite 06/18/26, checked in with manager on duty. Gained access to case model # RMNAMA serial # MY26B014985. Found temp at 41°. Manager stated that the door had been left open all night because door wouldn't close on its own. Adjusted door to close on its own. Allowed to cool down. Temp dropped to 37° and stalled. Removed inside rop panel to expose evaporator and fans. Fans are operational and there is no ice visible on coils. Reassembled and forced defrost incase there is any ice i couldn't see. Allowed to complete defrost. Refrigeration restarted. Case began to pull down to 35.7, until case attached satisfied. Then temp went up to 36°. Will return for further diagnosis.
|  |  | 2026-06-18 06:40 |  | Completed | 2026-06-19 | WO-0594225 | Tulsa, OK | Dollar General #14386 | Norman | OK | TAVANT/PRODUCT CARE | STORE CONNECT | TEMPERATURE |  |  |  | RLN2MA MY26B016452 |  | High temperature alarm | arrived onsite and assited tech in the removal of faulty micro block and installation on new all checks good Found unit temp at 58°f pull refrigerant out pulled vacuum and recharged 100g of r290 unit still not cooling properly called tech support on unit and they will send new unit to replace this one Returned to install new unit watched temp drop new unit working properly and re addressed to communicate with sc pulse
|  |  | 2026-06-18 02:08 | Tech was onsite 6/18 per his notes he must return | Return Needed |  | WO-0594191 | Southern | Dollar General # 13070 | Laurel | MS | TAVANT/PRODUCT CARE | STORE CONNECT | TEMPERATURE |  |  |  | RMN4MA/MY26B014986 |  | High temperature alarm
|  |  | 2026-06-16 03:39 |  | Completed | 2026-06-16 | WO-0593126 | Phoenix, AZ | Dollar General #22286 | Arizona City | AZ | 5108840 | FEXA | TEMPERATURE |  |  |  | RLN2MA MY26B014938 |  | Ice Cream is melting | Checked in with management upon arrival. Found unit down to temp at -6.0, pulled top panel to inspect the EVAP. It had no ice build up. Inspected the controller parameters. Found it has a defrost pre set of 45 min with a temp termination of 45F (7.2C), lowered the time to 20 min and 37F (2.7C). Put unit back together. Ran through a defrost cycle to verify. No further issues found. Unit temped -2 F before departure.
|  |  | 2026-06-16 02:19 |  | Completed | 2026-06-16 | WO-0592610 | San Antonio, TX | Dollar General #20761 | Pettus | TX | TAVANT/PRODUCT CARE | STORE CONNECT | TEMPERATURE |  |  |  | RLN2MA MY26B013813 |  | High Temperature alarm | I confirned unit was above temp at approx 16⁰F upon arrival. I verified controller, compressor and both condenser (1) and evaporator (2) fans were function. I confirmed coils were iced up. Checked with Hussmann to confirm theory of operation. I believe a power issue might have caused some controller issue because after a reset the defrost intiated (hot gas) without issue. I maually cleaned coil. I also sealed cracks/opening in the semas of the block. Issue is resolved.
|  |  | 2026-06-15 10:50 |  | Completed | 2026-06-23 | WO-0592045 | Tulsa, OK | Dollar General #23988 | Kingfisher | OK | TAVANT/PRODUCT CARE/5110636 | STORE CONNECT/FEXA | TEMPERATURE |  |  |  | RLN2MA MY26C025304 |  | High temperature alarm | 6/23 arrived onsite and replaed hot gas solenoid coil, ran coil thru factory wire casing, turned case, waistedf for case to get to decent temp for system to allow me to put through defrost and test solenoid, ran defrost solenoid worked, made sure temp got down to temp all checks good 6/16 arrived onsite foumd case evaporator iced up, after troubleshooting found hot gas solenoid coil not working has power but not energizing, case still under warranty, spoke to shane he will be filling out and providing the form for performance parts warranty, turned off case will return once part arrived to fix and turn on
|  |  | 2026-06-15 10:44 |  | Completed | 2026-06-15 | WO-0592039 | Houston, TX | Dollar General #20107 | Baytown | TX | TAVANT/PRODUCT CARE | STORE CONNECT | TEMPERATURE |  |  |  | RMN3MA MY26C025312 |  | High temperature alarm | 06-15-26 juan olvera technician dispatch send me one service call for the deer and milk case midel RMN3MA, serial number MY26C025312, first i drove to site job upon arrival check-in with manager, for next i found the case and set up the ladder to check the cases compressor, the case is working, i check the airflow, the coil, case temperature, compressors, and the door, i did not found anything wrong the case is working at 34 Fahrenheit, the defrost is working, condenser fan is working during refrigeration mode, for last i submit pictures in document and I explain to the manager my performance further more this call is complete.
|  |  | 2026-06-13 08:13 |  | Completed | 2026-06-13 | WO-0590801 | Phoenix, AZ | Dollar General #13396 | Coolidge | AZ | TAVANT/PRODUCT CARE | STORE CONNECT | TEMPERATURE |  |  |  | RLN2MA/MY26B016003 | X | High Temperature alarm on cases | Arrived at store checked in with manager checked microblock high temp alarm. After troubleshooting found a 2dr freezer microblock running at 10°F. Ran system through a defrost cycle and cleared out all frost that was on evaperator. Monitored unit after defrost. I did notice condenser temp was running arounf 140°F the store has no AC the are using portable ac units and store is really warm. Removed the trim covering condenser and condenser temp dropped to 129°F and temp inside case started to drop a little faster. Case is dropping case got down to 4°F but customers keep openning the doors and temps goes right up.
|  |  | 2026-06-12 10:51 |  | Completed | 2026-06-13 | WO-0590856 | Phoenix, AZ | Dollar General #22286 | Arizona City | AZ | 5097913 | FEXA | TEMPERATURE |  |  |  | RMN4MA/MY26B016036 | X | Freezer is shifting temperatures rapidly and ice cream is soft. Current at 16 degrees and warming. Need a tech sent asap! Thank you. | System was in Defrost mode, and case at 36f° when arrived, checked system for airflow and was low, I set system to another defrost to clear up, I also checked parameters and compare it to another case. I found dp1 at 60 min and dp2 at 45 min, so sinve these is hot gas I set it dp1 25 and dp2 at45, also dt1 and dt2 both where 48. Once defrost completed system returned to normal operation and I monitor temp drop til system rwached -1 we have good air flow and with the adjustment these case should be running accordenly now, I checked case was sealed and not getting moisture feom any where on top of case where system is set, no further issues upon departure. System went into eco mode at 2f° so I removed it from it.
|  |  | 2026-06-12 09:21 | ON HOLD | Unscheduled |  | WO-0589971 | Bolingbrook, Il | Dollar General #11509 | Harvey | IL | TAVANT/PRODUCT CARE | STORE CONNECT | COMMUNICATION |  |  |  | MY26B016494, RMN4MA/MY26B016536 |  | Communication loss on cases
|  |  | 2026-06-12 07:50 | ON HOLD | Unscheduled |  | WO-0589876 |  | Dollar General #22982 | Ropesville | TX | TAVANT/PRODUCT CARE | STORE CONNECT | COMMUNICATION |  |  |  | RLN3MA/MY26B016502, MY26B016013, RLN4MA/MY26B014967 |  | Communication loss on cases
|  |  | 2026-06-12 06:48 | ETA 6/15 | Unscheduled |  | WO-0590766 | Dallas, TX | Dollar General #21778 | Kaufman | TX | 5097125 | FEXA | WATER LEAKING |  |  |  | RLN3MA/MY26D028107 |  | Water is pouring down inside from the top - this has already been fixed once
|  |  | 2026-06-12 06:35 | ON HOLD | Unscheduled |  | WO-0589851 |  | Dollar General #22281 | Hamlet | IN | TAVANT/PRODUCT CARE | STORE CONNECT | COMMUNICATION |  |  |  | RLN2MA/MY26C019876, MY26B016513, MY26B16019 |  | Communication loss on cases
|  |  | 2026-06-11 09:03 |  | Completed | 2026-06-12 | WO-0588967 | Phoenix, AZ | Dollar General #22286 | Arizona City | AZ | TAVANT/PRODUCT CARE | STORE CONNECT | AIR LEAK IMPROPER DOOR SEAL |  |  |  | RLN2MA/MY26B014938 | X | having trouble with door leak impacting cooling performance | Arrived on site, checked in with manager. Found 2 door icecream case specified in WO description struggling to maintain setpoint with massive temperature swings when door is opened due to poor airlfow caused by a partially iced up evap coil. Ran system through 2 manual defrost cycles in order to completely clear this ice build up and reestablish proper airflow. Found cause of this to be that the defrost time was 15mins instead of 45mins and the termination temp was set at 38°F not 48°F as manufacturer recommended. Made these changes to manufacturer recommendations. Stayed and monitored system after defrost to ensure proper operation. Case is now running at and maintaning setpoint. No further issues found
|  |  | 2026-06-11 01:15 | HAVE SUZANNE TAKE A LOOK | Completed | 2026-06-12 | WO-5089345 | Phoenix, AZ | Dollar General #16435 | Tuba City | AZ | 5092946 | FEXA | ELECTRICAL |  |  |  | RMN4MA/MY26B013841 |  | Issue with eletric, need technician to return to reset | Return to power on units. New case powered on and achieved desired temp. All existing equipmwnt would not power back on and requires dollar general contractor to diagnose.
|  |  | 2026-06-11 |  | Completed | 2026-06-12 | WO-0589359 | Houston, TX | Dollar General #21135 | La Marque | TX | 5092945 | FEXA | WATER LEAKING |  |  |  | RMN3MA/MY26B016480 | X | Water is leaking under unit | 06-12-26 juan olvera tech dispatch send me one emergency service call for the beer case leaking water, first I drove to site job upon arrival check-in with manager, for next i remove the bottom panel to check where the water is coming from, the bottom of the case is clear, then i check the drain pan on top of the case and i found the drain pan full of water, so the wayer leaks because drains from the top to bottom, i drain the drain pan and i clean all the remain of the water, then i adjust the door torque rod for all 3 door the same beer case, also there was another water leak for the next frozen food case, i fix that water leak, the pump water hose was disconnect i explain to the manager the second case was not part of the call, for last i explain to the manager my performance, i submit pictures in document and this call is complete.
|  |  | 2026-06-10 | ETA 6/10 | Scheduled |  | WO-0588157 | Southern | Dollar General # 13069 | Laurel | MS | TAVANT/PRODUCT CARE | STORE CONNECT | TEMPERATURE |  |  |  | RMN4MA/MY26B014985 |  | High temperature alarm
|  |  | 2026-06-10 | ETA 6/11 | Materials Needed |  | WO-0588762 | Phoenix, AZ | Dollar General #14104 | Tucson | AZ | TAVANT/PRODUCT CARE | STORE CONNECT | AIR LEAK IMPROPER DOOR SEAL |  |  |  | RLN2MA/MY26B015990 |  | Frozen food 2 door having trouble with door leak impacting cooling performance
|  |  | 2026-06-10 | ETA 6/10 | Scheduled |  | WO-0588157 | Southern | Dollar General # 13069 | Laurel | MS | TAVANT/PRODUCT CARE | STORE CONNECT | TEMPERATURE |  |  |  | RMN4MA/MY26B014985 |  | High temperature alarm
|  |  | 2026-06-09 09:29 |  | Completed | 2026-06-10 | WO-0587865 | Davenport, IA | Dollar General #14341 | South Perkin | IL | TAVANT/PRODUCT CARE | STORE CONNECT | TEMPERATURE |  |  |  | RLN3MA/MY26B016495 |  | High Temperature Alarm | Checked ice cream freezer and new unit installed had no air flow. Evaporator has thick ice build-up. Checked defrost operation and was not passing power to hot gas defrost solenoid. Went through wiring and found both wires to naturals. Fixed wiring to power and ran through several defrost. Cleared ice buildup and cleaned water out of case. Put back together and back working in normal operation.
|  |  | 2026-06-09 04:30 |  | Unscheduled |  | WO-0587673 | Tulsa, OK | Dollar General #22799 | Amarillo | TX | 5086405 | FEXA | WATER LEAKING |  |  |  | RLN3MA/MY26B016006 |  | Water is collecting in the top of the cooler as well as inside the cooler. Lights go on and off they do not stay on.
|  |  | 2026-06-08 12:53 |  | Scheduled |  | WO-0586550 | Kansas City, MO (Lenexa) | Dollar General #2600 | Quincy | IL | 5082583 | FEXA | TEMPERATURE |  |  |  | RMN3MA/MY26D026820 |  | Not keeping the specified temperature, keeps going up and down
|  |  | 2026-06-08 10:11 | Door Gasket Needed | Materials Needed |  | WO-0586308 | Houston, TX | Dollar General #20654 | Alvin | TX | TAVANT/PRODUCT CARE | STORE CONNECT | TEMPERATURE |  |  |  | RLN2MA/MY26B016474 |  | High Temperature Alarm
|  |  | 2026-06-08 08:03 | 6/10 spoke with dispatcher they are trying to find a tech | Scheduled |  | WO-0586957 | San Antonio, TX | Dollar General #20761 | Pettus | TX | 5084774 | FEXA | LOW REFRIGERANT ALARM |  |  |  | RMN4MA/MY26B016036 |  | Observing low refrigerant operating condition
|  |  | 2026-06-08 12:53 |  | Unscheduled |  | WO-0586550 | Kansas City, MO (Lenexa) | Dollar General #2600 | Quincy | IL | 5082583 | FEXA | TEMPERATURE |  |  |  | RMN3MA/MY26D026820 |  | Not keeping the specified temperature, keeps going up and down
|  |  | 2026-06-07 08:32 |  | In Progress |  | WO-0585699 | Dallas, TX | Dollar General #3277 | Garland | TX | TAVANT/PRODUCT CARE/5080714 | STORE CONNECT/ FEXA | TEMPERATURE |  |  |  | RLN3MA/MY26D028108 |  | The alarm has been active beyond the configured threshold of 60 minutes.
|  |  | 2026-06-06 11:20 | DISASTER FIRE - NO BOS TICKET CREATED YET | Unscheduled |  | TBD | TBD | Dollar General #22711 | Purvis | MS | 5079187 | FEXA | DISASTER - FIRE |  | X |  |  |  | RFLN3/MY21D040973 - Unit caught fire - had to turn off | 6/8 - forwarded the service request to Eileen Petito, cc'd: Daniel Whited & Amber Fischer
|  |  | 2026-06-05 04:26 |  | In Progress |  | WO-0584971 | Kansas City, MO (Lenexa) | Dollar General #1247 | Trenton | MO | 5077040 | FEXA | TEMPERATURE | CASSETTE |  |  | RLN4MA/MY26C019909 | X | New unit...not holding temp | 6/4: Cassette was replaced on Thursday. 6/5: received service request from DG. 6/8: Tech found cassette low on refrigerant, to return on Tuesday to complete repair
|  |  | 2026-06-04 11:58 | DISASTER | Unscheduled |  | WO-0584133 | Charlotte | Dollar General #12955 | Surfside Beach | SC | 5074947 | FEXA | DISASTER - CASE ASSESSMENT |  | X
|  |  | 2026-06-04 10:30 | ETA 6/4 - Calculated Comfort | Completed | 2026-06-04 | WO-0583967 | RPM/Strategic Accounts | Dollar General #21342 | Klamath Falls | OR | TAVANT/PRODUCT CARE | STORE CONNECT | TEMPERATURE |  |  |  | RLN2MA/MY26C019880 |  | High Temp Alarm | Here are the hand written tech notes. We have not created an invoice yet for any charges. Our tech actually found other problems on site that need attention. Freezer 10 11 and 12 are experiencing drain pump issues...these are the old freedom cases. We are requesting a work order for a return visit to replace the drain pumps. Also another work order for a follow up on the micro block freezer to check the refrigerant charge. They defrosted the frozen evaporator and checked the operation. It is operating correctly at this time. We are requesting another work order for a follow up visit at the same time we replace the pumps on the freedom cases. When our tech got there the pumps had failed to the point there was water on the floor. Thanks, Dave Calculated Comfort
|  |  | 2026-06-04 09:39 |  | Completed | 2026-06-08 | WO-0584430 | Kansas City, MO (Lenexa) | Dollar General #21709 | Eolia | MO | 5074861 | FEXA | DOOR |  | X |  | RMN3MA MY26D029152 |  | Door remains open or sparks | (CS) Found the system wouldn't call for cooling. I checked to make sure the safeties were good and they were. System had freon. I went to try and change the setpoint on the controller, and it was stuck on 178 degrees. I tried to reset and change it and it wouldn't change. Controller needs replaced on this cooler. Submitted parts request for new controller. Come to find out the case is not under warranty and they need to use their normal service contractor. Job is complete on our end NOTE: naissance call on the MY26 case as someone had already fixed and Hussmann was asked to look at a non-warranty case.
|  |  | 2026-06-04 01:43 | DISASTER | Unscheduled |  | WO-0584141 | RPM/Strategic Accounts | Dollar General #14306 | Sacramento | CA | 5074878 | FEXA | DISASTER - REMOVAL DISPOSAL |  | X |  |  |  | Store is closing and need refrigeration removed and disposed of.
|  |  | 2026-06-03 22:14 | Internal Purposes Only | Unscheduled |  | WO-0583750 | RPM/Strategic Accounts | Dollar General #1247 | Trenton | MO | TAVANT/RPM INSTALLATION | SUZANNE | CASSETTE, REPLACEMENT | CASSETTE |  |  | RMN4MA/MY26B016036 |  | Low Refrigerant Operation Condition | **Andrew Miller mentioned cassette replacement, RPM/Rob Starkey stated, failure occurred during start up & waiting for details/equipment information**
|  |  | 2026-06-03 09:41 |  | Completed | 2026-06-08 | WO-0583216 | Tulsa, OK | Dollar General #20336 | Ardmore | OK | 5071633 | FEXA | TEMPERATURE |  |  |  | RLN2MA/MY26B015996 |  | Flashing HA - Up to 28 degrees | Case RLN2MA / S/N MY26B015996 is working correctly setpoint is -10 degreees and is at -9.0 degrees. Verified fans / lights / compressor is working correctly with no alarms present on case. Case is holding temp with no issues. Note: Nextech HVAC/R is here at store working on case next to this one.
|  |  | 2026-06-02 10:04 |  | Completed | 2026-06-08 | WO-0583040 | Houston, TX | Dollar General #20440 | Sheridan | TX | 5069343 | FEXA | ICE/FROST & LOW REFRIGERANT |  |  |  | RLN3MA/MY26B016036 |  | Ice build up and Low refrigerant | Picked up insulation, silicone, and butyl foam from Uri. Arrived on site, spoke with Mic, and found that one door was sweating and causing the frame to ice over. Found that the anti-sweat function of that door wasn't working, but the other two were. Checked wiring and connections in the raceway and found that the heater plug wasn't fully plugged in. Once I tightened the connection, the heaters on the door started to work. Also insulated and siliconed the top of the box due to air infiltration. The case is now running and operating as designed, and cases are meeting the setpoint of -9 degrees.
|  |  | 2026-06-02 10:03 |  | Canceled | 2026-06-03 | WO-0583039 | Kansas City, MO (Lenexa) | Dollar General #21709 | Eolia | MO | TAVANT/PRODUCT CARE | STORE CONNECT | TEMPERATURE |  |  |  | RLN2MA/MY26B016465 |  | Hight Temperature Alarm | Store Connect canceled call stating everything was normal
|  |  | 2026-05-30 04:57 |  | Completed | 2026-05-31 | WO-0580974 | Southern | Dollar General #21415 | Sulphur | LA | 5060356 | FEXA | TEMPERATURE | PRODUCT LOSS - EXISTING CASES | X |  |  |  | Invalid Temperature reading- cases running warm - RLN2MA/MY26C019877 & RLN3MA/MY26D029648 | Hussmann Cooler MODEL ID: RFMN5 SERIAL NO MY20D029072 Hussmann Freezer SERIAL NO MY20D029045 MODEL ID: RFLN4 Arrived onsite and spoke with the manager. Inspected the cooler and freezer cases that were experiencing temperature issues. Found the freezer controller setpoint was incorrectly set to 32°F. Adjusted the setpoint to -8°F to match the adjacent freezer case. Syatem recovered to -7 degrees upon departure. Inspected the cooler case that was running at elevated temperatures and located a refrigerant leak at the liquid line hose flare fitting. Loosened the fitting, applied thread sealant, and retightened the connection until the leak was eliminated. Leak detector readings decreased from approximately 500 ppm to 0 ppm, confirming the repair. Added 1.5 lbs of R-448A refrigerant to the system. Upon departure, the cooler temperature recovered from 44°F to 40°F. Also found the adjacent cooler case setpoint incorrectly adjusted to 230°F; reset the controller to 34°F. The cooler temperature recovered from 68°F to 51°F prior to departure. Both cases are operating and cooling properly at this time. Due to elevated product temperatures, full temperature recovery is expected to occur overnight as the product load continues to cool. Caleb S
|  |  | 2026-05-30 03:30 |  | Completed | 2026-06-01 | WO-0580946 | Southern | Dollar General #6372 | Petal | MS | 5060355 | FEXA | TEMPERATURE |  |  |  | RLN3MA/MY26C019883, RMN4MA/MY26B016031 |  | Not Keeping Specified Temp | RMNAMA Serial #MY26B01603, cycled power to both units. Units back online, temps ok. RLN3MA Serial #MY26C019883, cycled power to units, back online. Temps ok.
|  |  | 2026-05-29 09:34 |  | Completed | 2026-05-29 | WO-0580073 | Houston, TX | Dollar General #20582 | Houston | TX | TAVANT/PRODUCT CARE | STORE CONNECT | TEMPERATURE |  |  |  | RLN3MA/MY26B014956 |  | High Temperature alarm | Arrived on site checked in with manager. Found frozen food case running warm but not in alarm. After further inspection found left door not closing properly. Adjusted door and it is now closing as intended. Also noticed ice build up on left hand return air penetration. Ran both condensing units through defrost and removed ice. Checked top of case and found wet spot between micro block and top of case. Cleaned water and use silicone to seal between case and micro block. Put case back together and waited for case to reach set point. Checked out with manager work order complete
|  |  | 2026-05-29 04:37 | ETA is 6/1 | Scheduled |  | WO-0580512 | Davenport, IA | Dollar General #14347 | South Perkin | IL | TAVANT/ANDREW MILLER | ANDREW MILLER | WATER ICING ISSUE
|  |  | 2026-05-26 12:31 | DISASTER | Unscheduled |  | WO-0578039 | RPM/Strategic Accounts | Dollar General #12799 | Wichita | KS | 4988413 | FEXA | DISASTER - MOVE CASES |  | X |  |  |  | Below are the details for a new service call. o Site Name/#: Dollar General 12799 o Address: 1624 E Central Ave Wichita, KS o Store Hours: 8am – 9pm (store will not stay past closing) o NTE: $1,500 o PO: 4988413 o Problem: Check In/Out with Store **need this 5 door Hussmann cooler unit moved out 4-5 ft in order to complete interior repairs. Units need to stay powered on, if possible. Building has large hole on the side of building. Coolers in front of large hole no one can get in form hole, but maybe an animal could. Manager on Duty OBTAIN A SIGNATURE ON SERVICE TICKET & NOTE FIRST AND LAST NAME. Hussmann Equipment ONLY: <insert issue> Tech can work on multiple Hussmann Cases with one ticket, confirm all cases are operating or diagnose before leaving the store. Tech must list or take pictures of the data tag of all equipment model/serial number repaired on service ticket and provide a detail work summary of each equipment repaired. If you need assistance, please contact Hussmann Technical Support @ 800-922-1919, option #3. If Parts are needed, contact Hussmann Warranty Parts @ 855-487-7778, option #6 – state it’s for Dollar General Copeland compressors are under warranty over the counter through United or Copeland Distributor. Sanhua TXV replacement is not available – source Sporlan. If parts are not available & have long lead time, send us an e-mail @ dg.service@hussmann.com to help locate. Invoices must be sent within 30 days of repair completion date to both April.marolf@hussmann.com and the dg.service@hussmann.com emails. Send repair status with a brief work summary BEFORE leaving the location to dg.service@hussmann.com. If you have any questions, contact us at @ dg.service@hussmann.com Troubleshooting Process Step 1 - Start with documentation located within case Operation Manual & Data Sheet with the case. Step 2 - Scan Hussmann QR Code located on model/serial plate Type serial number of case and follow navigation for product sheets, data sheets, and manuals Step 3 – Scan BOX QR Code for Box account Carries in depth support - parameters, controller guides etc. Step 4 - Contact technical support - direct line #866-785-8499 Tech support will escalate to our Field Equipment Team if issue cannot be resolved – tech support does not provide NTE/OT approval A qr code on a white background AI-generated content may be incorrect. A qr code with a box AI-generated content may be incorrect.
|  |  | 2026-05-23 09:24 |  | Completed | 2026-05-23 | WO-0576129 | Houston, TX | Dollar General #6996 | Baytown | TX | TAVANT/PRODUCT CARE | STORE CONNECT | TEMPERATURE |  |  |  | RMN4MA/MY26D028118 |  | High Temperature Alarm | 5/23/26 Checked in with management , walked store and found a cases at temp , checked all cases ID tag to verify case called in running warm , located case and found case at temp , checked air flow , spoke with management and found out store experienced a power outage do to storm , all case back online and at temp , all checks out at this time.
|  |  | 2026-05-22 07:57 | 6/8 Tech scheduled for 6/18 6/2 Andrew is sending parts to tech 6/1 checked with brach. Tech reached out to Andrew 5/22 and is waiting for response. Pinged Andrew. | In Progress |  | WO-0575409 | Phoenix, AZ | Dollar General #10339 | Casa Grande | AZ | 5036631 | FEXA | TEMPERATURE |  |  |  | RLN2MA/MY26B016459 (same case from 5/5) |  | 5/22 @ 7:57am - Check In/Out with Store Manager on Duty & Obtain Signature Hussmann R290 Microblock Equipment ONLY: RLN2MA, MY26B016459 Not working at all. • TECH must obtain a photo of the equipment tag that includes MODEL & SERIAL number on the CASE & CONDENSING UNIT (Tecumseh) • Tech can only work on multiple Hussmann R290 cases with one ticket, confirm all cases are operating or diagnose before leaving the store. • DO NOT work on existing cases, communicate to the Store MOD to place call with their service vendor. • Tech must list or take pictures of the data tag of all equipment model/serial number repaired on service ticket and provide a detail work summary of each equipment repaired. • If you need assistance, please contact the following Hussmann Technical Support Team @ 866-785-8499 or the following: 1. Todd Green @ 210-346-0005 2. Jeff Fosnaugh @ 314-501-8736 3. Andrew Miller @ 314-501-8698 • Hussmann Performance Parts @ 855-487-7778, option #3 – Warranty • Tecumseh compressor warranty – supply house will provide warranty tag to fill out & obtain a copy for office. Must purchase the compressor & file warranty claim. • If parts are not available & have long lead time, send an e-mail @ dg.service@hussmann.com to help locate. • Invoice MUST be submitted within 45 days of repair completion date to TAVANT. For support with warranty claim @ 800-398-7402, option #4 or hussmannwarrantyclaims@hussmann.com Send repair status with a brief work summary BEFORE leaving the location & contact to dg.service@hussmann.com. If you have any questions, contact us at @ dg.service@hussmann.com Troubleshooting Process Step 1 - Start with documentation located within case • Operation Manual & Data Sheet with the case. Step 2 - Scan Hussmann QR Code located on model/serial plate • Type serial number of case and follow navigation for product sheets, data sheets, and manuals Step 3 – Scan BOX QR Code for Box account • Carries in depth support - parameters, controller guides etc. Step 4 - Contact technical support - direct line #866-785-8499 • Tech support will escalate to our Field Equipment Team if issue cannot be resolved – tech support does not provide NTE/OT approval. | Found 2 door freezer high temp at 33 degrees. Found no air flow to case. Found evaporater iced up. Ran system theough serveral defost and used hot water from spray pump. Found case not draining. Drain line was plugged with foam spray inside drain line. Was able to remove with long screwdriver. All defrost operations working properly. Found right door gasket laying over and not sealing properly Need new door gasket. Possible micro block may need new seal around cabinet. Got unit back on line and monitored temps. D/A 5.3 degrees and dropping. Alarm clear on departure. Need to f/u on system to make sure system is defrosting properly
|  |  | 2026-05-22 06:03 |  | Completed | 2026-05-22 | WO-0575297 | Phoenix, AZ | Dollar General #19997 | Buckeye | AZ | TAVANT/PRODUCTCARE | STORE CONNECT | DOOR |  |  |  | RMN4MA/MY26B016517 | YES | 5/22 @ 6:07am - Response : Priority: P1-Immediate Job Scope: HIGH TEMPERATURE Tech must obtain a photo of the equipment tag that includes Model & Serial Number on the Case and Condensing Unit (Tecumseh). Please review and Confirm the Checklist items below: We are observing a High Temperature Alarm on the Serial number MY26B016517, RMN4MA, Left & Center/Right Microblock case at the above-mentioned location. The alarm has been active beyond the configured threshold of 60 minutes. The store is currently operational and fully stocked with products. If this condition is not addressed immediately, it may result in product loss, food safety risk, and significant store operational impact, potentially leading to customer dissatisfaction. To prevent any product loss and ensure continued store operations, we request an immediate P1 (Critical) level site visit. Checklist: • Inspect the evaporator coil for ice or frost accumulation • Verify the evaporator fan is active and running properly • Confirm airflow direction and un-obstructed air circulation • If ice is present: Perform a manual defrost to fully clear the evaporator coil • Verify Hot Gas Valve operation during defrosts • Confirm the condenser fan turns OFF during defrost • Verify the refrigerant charge level • If low, charge the system to the manufacturer-recommended level | Found left side of case high temp alarm. Found left door open on arrival. Had to adjust torque rod to get door to close properly. Monitored temps. D/A 38 degrees and dropping. Alarms clear on departure Resource: Ramond Ramirez Found left side of case high temp alarm. Found left door open on arrival. Had to adjust torque rod to get door to close properly. Monitored temps. D/A 38 degrees and dropping. Alarms clear on departure Resource: Ramond Ramirez
|  |  | 2026-05-20 12:41 |  | Completed | 2026-05-21 | WO-0573996 | Houston, TX | Dollar General #20107 | Baytown | TX | 5031411 | FEXA | CAREL CONTROLLER, PROBES | PRODUCT LOSS - 2 LT, ICE CREAM |  |  | RLN2MA/MY26B015992 (not pulling up in PP) |  | Not working at all - all the ice cream is melted | 5/21/26 I arrived and spoke with the manager. Read the alarms on the carel aplica mobile app, alarms listed were probe 1, probe 2, & control probe fault. Called Hussmann tech support. Found, the probe 1, probe 2, & control probe— plug disconnected from the controller. Disconnected the power to the unit, plugged in that said- plug to the respective receptacle on the controller, reconnected the power, watched the case pull down, currently the case is at 0.5° Fahrenheit, no longer in alarm, and pulling down to temperature setpoint. Remounted and re-fastened the cover over the control box. Cassette Model# ALX44U-DS3B01 Serial# 04E0226121673 Case Model# RLN2MA Serial# MY26B015992
|  |  | 2026-05-20 02:19 | Suzanne Finding Someone to Run | Unscheduled |  | WO-0574005 | RPM/Strategic Accounts | Dollar General #21223 | Santa Anna | TX | 5031586 | FEXA | ICE/FROST |  |  |  | RLN2MA MY26B014946 |  | Starting to Drip Frozen
|  |  | 2026-05-18 05:55 |  | Completed | 2026-05-19 | WO-0572389 | Kansas City, MO (Lenexa) | Dollar General #7231 | Springfield | MO | 5021320 | FEXA | NOISE |  | X |  |  |  | Case is making a beeping sound | Checked in with manager. Upon arrivial i found only one case not operating and it is a medium temp case. The serial number is not a MY26 it is a MY19. I talked to hussmann warranty department and found out this case is NOT under warranty. I was instructed to not work on this unit because its not under warranty.
|  |  | 2026-05-17 08:30 |  | Completed | 2026-05-17 | WO-0571130 | Bolingbrook, IL | Dollar General #20597 | Chicago | IL | TAVANT/PRODUCT CARE | STORE CONNECT | TEMPERATURE |  |  |  | RLN3MA/MY26B016493 | YES | Response : Priority: P1-Immediate(0-24 Hours) Job Scope: HIGH TEMPERATURE We are observing a High Temperature Alarm on the Serial number MY26B016493, RLN3MA, Left/Center/Right Microblock case at the above-mentioned location. The alarm has been active beyond the configured threshold of 60 minutes. | Drove to store, checked in with manager. On site for 3 door frozen unit running warm. Upon inspection found center door being held open by right hand door door heater wire bushing that hand come out of door frame. Reinstalled. Cleared ice around door. Door now closing properly forced defrost on both units to clear any frost build up on evaporator. Coils clear, defrost operation normal. Case now has good airflow. And at setpoint. Work complete.
|  |  | 2026-05-16 10:06 |  | Completed | 2026-05-15 | WO-0570321 | Dallas, TX | Dollar General #21778 | Kaufman | TX | 5012792 | FEXA | WATER LEAK |  |  |  | RLN3MA/MY26D028107 |  | Leaking Water and forming on all products inside | May 18 2026. Checked in with manager kelly hunter. Work order was for water leaking inside the case. Located case. Verified case was microblock and took pictures of case and condensing unit data tags. Saw that there was ice on one of the glass doors as well as on the shelves and the ceiling of the case. Verified door heaters were operational. Cleared ice from the door. I then removed the ceiling to see where water might be coming from. Found ice buildup underneath where the drain line leaves the case and goes to the condensate pan under the condensing unit. Checked condensing unit. Found a pile of bolts and screws inside the condensate pan blocking the drain line. Removed the obstruction then put case in defrost. Defrost operational. I found water leaking out from the area where the drain leaves the evaporator. Used silicone sealant to seal around the area. Water stopped. I then took case out of defrost. Had manager remove product from shelves so i could clear the ice off. Put case back together. No other issues found. Checked out with m.o.d
|  |  | 2026-05-15 02:48 |  | Completed | 2026-05-20 | WO-0570508 | Kansas City, MO (Lenexa) | Dollar General #14928 | Nixa | MO | TAVANT/PRODUCT CARE/INSTALLATION | RPM/ROB S. | ELECTRICAL |  |  |  | RLN2MA/MY26D02809, RLN3MA/MY26D03141 |  | Cases were recently installed & no longer working…customer schedule to have product delivered tomorrow.
|  |  | 2026-05-13 08:38 |  | Completed | 2026-05-18 | WO-0569146 | RPM/Strategic Accounts | Dollar General #21130 | White City | OR | 5008372 | FEXA | ICE/FROST |  |  | FR54400 | RLN3MA/MY26C019887 | YES | There is a block of ice on the inside at the top of the unit, Not keeping the specified temperature | Evaporator leaked water down inside the case. We chipped off the ice out of the case. We found that the drain was pointed upwards because wire conduit was run below the drain line. We re-ran the conduit above the drain to the lower the drain tube.
|  |  | 2026-05-13 08:13 |  | Completed | 2026-05-14 | WO-0568891 | Southern | Dollar General #21375 | Oxford | AR | 5006558 | FEXA | TEMPERATURE |  |  | FR54401 | RLN3MA/MY26B013828 |  | Invalid Temperature Reading | Arrived to check the 3 door freezer case for being high temp. Found it running defrost far to long for being hot gas. Found the parameters on the controller were not correct. Adjusted as necessary. Pulls down much quicker after defrost now. Job complete.
|  |  | 2026-05-13 03:25 | DISASTER 5/29 emailed team for an update 5/14 Jerry sent email requesting survey | Accepted |  | WO-0569339 | Gulf | Dollar General #25390 | Homer | GA | 5008919 | FEXA | DISASTER - DAMAGED UNITS |  | X | FR54399 | RFLN4/MY23K092022, RFLN5/MY23K092026 |  | VH & units damaged- need to dispatch for replacement; Per Nextech - The cases have been patched up as well as could be. There are still air penetrations and ice forming in different spots on the case, including the back side. The impact looks to have been sufficient that I would say that the insulation between the paneling has been broken apart. I don’t see them as fully repairable. Thanks, Kendra
|  |  | 2026-05-12 11:53 |  | Completed | 2026-05-13 | WO-0568437 | Phoenix, AZ | Dollar General #22286 | Arizona City | AZ | TAVANT/PRODUCT CARE - RECALL | STORE CONNECT | ICE/FROST |  |  |  | RLN2MA/MY26B014938 | YES | RECALL - issue still persists - coil icing | Arrived at store and checked in with manager. Upon arrival the case hasno visible signs of icebuild up. Opened top panel inside of the case and checked evap coil and found the top half of the coil was iced up. Ran case through multiple defrost to clear ice and defrost sensor never showed above 31 degrees. Checked over micro block unit and noticed there was alot of water coming out of the liquid line penitration. The penitration isnt fully sealed to the outside. Shut unit down. Removed microblock box over evap coil and found the end of the coil is still iced up. Deiced the rest of the coil and checked sensor locations are both correct and defrost sensor was covered in ice which explains why it wouldnt go any higher. Applied more butyl to the bottom of the box along with over the line penitrations to seal them both. Reset box over evap coil and started unit back up. Case is now back down to temp and defrost time has been adjusted to 45min from 40 minutes to help keep the coil clear.
|  |  | 2026-05-12 11:49 |  | Completed | 2026-05-14 | WO-0568430 | Houston, TX | Dollar General #14858 | Houston | TX | TAVANT/PRODUCT CARE - RECALL | STORE CONNECT | REFRIGERANT, LEAK |  |  |  | RLN3MA/MY26B016004 | YES | RECALL - issue still persists - lack of refrigerant | Checked in. Located case matching serial number from work order. Found 3 door rif at -5 degrees on both controllers. Found no alarms. Could not leak check due to unit is R290 and my leak detector does not have the sensor for it. At e2 did not see any refrigerant leak alarms. There were no active alarms on controller. Spoke with manager, per manager wo was for an older system, breakfast case. That case was at temp. Advised them to open a separate wo for that case and serial number. RIF is operating as of now.
|  |  | 2026-05-12 11:46 |  | Completed | 2026-05-13 | WO-0568428 | Phoenix, AZ | Dollar General #22613 | Hereford | AZ | TAVANT/PRODUCT CARE - RECALL | STORE CONNECT | REFRIGERANT, LEAK |  |  |  | RLN2MA/MY26B014941 |  | RECALL - issue still persists - lack of refrigerant | Frozen meats Checked in. Located case matching serial number from work order. Found 3 door rif at -5 degrees on both controllers. Found no alarms. Could not leak check due to unit is R290 and my leak detector does not have the sensor for it. At e2 did not see any refrigerant leak alarms. There were no active alarms on controller. Spoke with manager, per manager wo was for an older system, breakfast case. That case was at temp. Advised them to open a separate wo for that case and serial number. RIF is operating as of now.
|  |  | 2026-05-12 11:38 |  | Completed | 2026-05-13 | WO-0568415 | Phoenix, AZ | Dollar General #14104 | Tucson | AZ | TAVANT/PRODUCT CARE - RECALL | STORE CONNECT | ICE/FROST |  |  |  | RLN2MA/MY26B015990 |  | RECALL - Issue still persists - coil icing | Dwain Taylor - Tech Notes Arrived on site checked in with site manager Located unit in question documented case temp Upon arrival at −6.3° continued inspection verified airflow was adequate , clear and unobstructed continued inspection verified condenser coil is clean verified compressor was pulling correct amperage verified that unit top Evaporator cover was sealed with no loss of air flow at this time ran system through manual defrost verified operation of defrost is correct verified time of defrost and termination is correct verified restart of unit watch temperature drop temperature dropped approximately to −8.8° Found no issues with this unit at this time..
|  |  | 2026-05-12 06:31 | 5/13 Per Suzanne send to Specrite 5/13 Per Ashley she is checking with management and getting a tech out | Completed | 2026-06-02 | WO-0568707 | RPM/Strategic Accounts | Dollar General #31905 | Grand Prairie | TX | DEVIN SUMMERS/TIM SMITH | TIM SMITH | TEMPERATURE |  | X |  | RFLN3/MY24A007599, RFLN4/MY24B011485 |  | Hussmann Freedom Line 3 total cases – out of warranty: Two Freezer Cases RFLN3/MY24A007599 – RFLN4/MY24B011485 have no digital temperature reading & don’t know what the temperature suppose to be. One Cooler Case RFMN3/MY22B019861 is reading 48 degrees and the breaker boxes are not labeled. Confirm cases are programmed, operational & correct temperature.
|  |  | 2026-05-12 04:15 | 5/12 Suzanne determining who will run | Completed | 2026-06-02 | WO-0568634 | TBD | Dollar General #3270 | San Angelo | TX | TAVANT/PRODUCT CARE - RECALL | STORE CONNECT | REFRIGERANT, LEAK |  |  |  | RLN3MA/ MY26B016488, CENTER/RIGHT |  | RECALL - issue still persists - lack of refrigerant | Per Suzanne - Store reports no issues, close ticket
|  |  | 2026-05-10 03:45 |  | Completed | 2026-05-10 | WO-0567300 | Phoenix, AZ | Dollar General #22864 | Tucson | AZ | TAVANT/PRODUCTCARE | STORE CONNECT | TEMPERATURE |  |  |  | RLN3MA/MY26B014958 |  | RLN3MA MY26B014958 ALARM SHOWING HIGH TEMPERATURE | Arrived manager stated the line up on the east side of wall frozen foods is not hold temp also the right corner 4 door case with 2 condensors. Checked the set points for the right corner line up and they were all set to 23 degrees. Went into control and placed set point based off manufacture recommendations -5. Temps started to come down. The corner 4 door case the controller kept on reading 0000. Tried to get through controller to enter passcode to view set points was unable to set set points at time went ahead and disconnected controller and reconnected then display came on and worked to change set point to -5. Temps on that case began to come down. Condensor fans are spinning along with evap fans. Did not see potential leaks used leak detector. Placed into manuel defrost and condensor fans shut off. Cleaned condensor coils with nitrogen on all condensors on right wall line up and 4 door right corner case
|  |  | 2026-05-08 09:11 |  | Completed | 2026-05-08 | WO-0566374 | Grand Rapids, MI | Dollar General #20639 | South Bend | IN | TAVANT/PRODUCT CARE | STORE CONNECT | TEMPERATURE |  |  |  | RLN3MA/MY26B016016 | YES | HIGH TEMPERATURE | When I arrived the cases were at 5 degrees. Checked for air obstruction and it seemed to be fine. One of the doors was not tensioned and there was reason to believe it was left open which caused the alarm. I tightened the door so it now closes properly and the cases were -3 when I left.
|  |  | 2026-05-06 |  | Completed | 2026-05-08 | WO-0565337 | Tulsa, OK | Dollar General #21606 | Porum | OK | TAVANT/PRODUCT CARE | STORE CONNECT | TEMPERATURE | PRODUCT LOSS - 3 LT, FROZEN FOOD |  |  | RLN3MA MY26B013826 |  | HIGH TEMPERATURE Product line Serial Number Module Assets Model Alt Name: Microblock MY26B013826 Left RLN3MA Frozen food 5 Center/Right | 5/8 Arrived on site and checked in. Unit had cleared a lot of water and was tmde iced. Turned back on and turned back on lights and antisweats. Unit pulled right down to temp, cycling normally. Has defrost operating normally. Spoke with jeff and decided that if unit ices up again in the future we will replace removable deck unit with a new one. WO complete. 5/7 Tried to de ice system but there is significant ice build up on coil. Due to design of microblock units i could not manually de ice. Had to shut off unit and will return on Friday morning to turn back on after ice has melted out.
|  |  | 2026-05-05 10:51 |  | Completed | 2026-05-06 | WO-0564555 | Phoenix, AZ | Dollar General #10339 | Casa Grande | AZ | TAVANT/PRODUCT CARE | STORE CONNECT | TEMPERATURE |  |  |  | RLN2MA MY26B016459 |  | We are observing a High Temperature Alarm on the Serial number MY26B016459, RLN2MA, Left Microblock case at the above-mentioned location. The alarm has been active beyond the configured threshold of 60 minutes. | 5/5 Arrived at store and checked in with manager. Made my way back to new 2door microblock freezer. Found it was running warm due to all the product stuck inside the case. All the product is blocking the air flow. Store had to over load the case due to the one of the 3 door freezers being down. Also the cant use their over flow freezer in the back room because the electrician changed the outlet for it from a twist lock to a normal 3 prong plug. Ran case through 2 long defrost to male sure the evap coil is clear of ice. Temp is at 10 degrees upon departure. Will follow back up once new controller for the down 3 door arrives.
|  |  | 2026-05-05 |  | Completed | 2026-05-06 | WO-0564924 | Phoenix, AZ | Dollar General #13631 | Quartzsite | AZ | TAVANT/J BUDIK | RPM/SUZANNE B. | NUISANCE |  |  |  | RMN4MA/MY26D028116 | YES | Hussmann R290 Microblock Case: Beverage Case – RMN4MA, possible undercharged and/or refrigerant leak. Tech must pick up R290 before heading to store. | Upon arrival found everything working proper, customer stated someone was here this morning and was doing something on top but didn't know who or what, leak checked eberything and no leaks found. Monitored operation for a dozen cycles and both condensers turn on @40* and shut off @30*, checked all electrical connections, evaporator coils and motors, checked condenser coils and motors. Refrigeration cycle from 40* to 31* is 4.5 minutes. All pictures are attached in BOS.
|  |  | 2026-05-02 07:40 | Installation Team handled | Completed | 2026-05-05 | WO-0563528 | Phoenix, AZ | Dollar General #13396 | Coolidge | AZ | 4983001 | FEXA | CASSETTE | BMS PLUG |  |  | RLN2MA MY26B016003 |  | Not working at all. Lights on unit warm inside. | 5/5There’s been some miscommunication from the factory to installation team for this location… Please DO NOT order BMS plug, this will be addressed by the Installation Team. Close out ticket, submit to Tavant: add note to description of claim – Sales/Factory did not add the BMS Plug to 2 Door Case replacement shipment & another order was placed without knowledge to service team before customer placed the service request. 5/4 Arrived at store and checked in with manager. Made my way over to hussmann 2 door freezer. Found the breaker on the electrical box was turned off. The installer also removed the BMS plug for the sensor/communication wire and I believe that is why they left the breaker off. Turned breaker on and monitored case and it has dropped down to 0.6 degrees and still dropping. Cycled case through defrost as well no issues found. Will get new BMS plug ordered and follow up to replace.
59e6d1e0-4743-f111-88b4-70a8a59001d5 | 5fwVqsBfxF8ffzogfVx71CXSfzifEdaEI+87xbb0fc8BN+hr8nDT75EadCNoX1zp9qeQGF4pvNVVteaRvrNdpQ== | 46141.6202 | 2026-04-28 14:19 | DISASTER 5/29 sent email to team for update 4/29 Jerry creating quote | Pending Quote |  | WO-0561350 | RPM/Strategic Accounts | Dollar General #24243 | Starkville | MS | 4971334 | FEXA | DISASTER: CASE(s) REPLACEMENT & INSTALLATION | CASES | X |  |  |  | Dollar General requesting Hussman's Assistance: Due to car hit damage, Nextech has advised: ALL 3 Of Units needing replacements RIF1 HUSSMAN MY22H084731 RFLN5 RIF 2 HUSSMAN MY22K088659 RFLN4 RIC4 HUSSMAN MY22K090785 RFMN4 Please dispatch for replacement. Thanks, Kendra
1470bcbf-3b43-f111-88b4-70a8a59001d5 | E7KM7qXbsdfpvfJwveq/VdTqahZc/5yTtZlwSarywFxAfNNnQ1wzrL3nfHYG8LqLe0EyU4cbgT8pXadn/6cucg== | 46142.7437 | 2026-04-28 12:52 | CASE ASSESSMENT ETA is July 5/8 Quote entered into FEXA & APPROVED 5/1 Tech did assessment, waiting on quote or further direction | Materials Ordered |  | WO-0561294 | Charlotte, NC | Dollar General #9929 | Townville | SC | 4970415 | FEXA | CASE ASSESSMENT |  | X |  |  |  | Hussmann Cases – 5 qty Cases: RFLN4/MY23f057380 ~ RFMN4/MY23h081991 ~ RFLN4/MY23C028835 Ice cream ~ IDF5SM8TE/MY23g064419 Open Air Meat & IDF5SM12TE/MY23HO73441 Open Air produce: Tech must perform a thorough inspection of each case, take pictures of any damage/findings (water leak/refrigerant leak/damage, ect…) and list repairs needed for each case. Look below for items to check for on the cases and previous repairs performed by others. Any questions, contact Suzanne/Hussmann Account Manager @ 206-255-7674. Items to look at: - Store temperature & Humidity by the cases - Any air from vents/door on the Open-Air Cases - Check case temperatures - Defrost - Programming of controller, ensure it’s program to spec - Product is below the product line/not blocking vents - Reach in doors closing/sealing properly & gasket in good condition - Condensate drain/pan conditions - List repairs needed for each case, need to submit proposal - Tech MUST take pictures of any damage/findings (leaking water, refrigerant leak, damage to case, ect…) • IDF5SM12TE/MY23HO73441 Open Air cooler produce? o 11/19/24-11/21 replaced fan blade o 11/29/24-12/16 compressor o 2/12/25-2/12 condensate pump line clogged o 3/24/25-3/26 condensate pump line air bubble o 5/15/25-5/16 water leaking. Tech found nothing. o 5/31/25-6/5 frozen over and making noise. o 6/22/25-6/27 frozen due to fan shroud off. o 7/3/25-7/7 fan clanging and water leaking. Cleared tubing again o 7/12/25-7/15 water pan full again. Tech shortened hose again o 7/15/25-7/16 duplicate o 7/30/25-8/6 cooler basin full of water AGAIN o 8/8/25-8/11 replaced condensate pump o 10/30/25-11/18 leaking. Replaced condensate pump o 3/12/26-3/16 leaking. Replaced condensate pump o 4/15/26 tech found unit leaking and fixed on site same day. • IDF5SM8TE/MY23g064419 Open Air meat cooler o 2/19/26-2/20/26 water leak. Condensate pump cleaned and tubes. o 4/14/26-4/16/26 pump replacement • RFLN4/MY23C028835 Ice cream walk in o 7/12/25-7/27 replaced terminal o 8/11/25-8/13 replaced contactor and controller o 8/28/25-8/30-8/29 ice build up between doors. o 10/31/25-11/6 ice build up between doors. Rewired. o 11/14/25-11/18 replaced condensate pump o 1/15/26-1/19 tightened wires. Puddles and freezing o 3/1/26-3/12 replace door frame heaters o 3/16/26-3/19 not holding temp. fixed wiring o 4/6/26 open ticket. Replacing frame heater leaking. • RFLN4/MY23f057380 • RFMN4/MY23h081991
d4d7c48b-4642-f111-88b5-000d3a57f875 | 6ijwTb/9fTwly/teL3uyRmAyl9r2IiwPgeyuu995of7NElE4XxQP0ThQqA9kfwKEQdf3Zf7iKyrWaFaPq4z9vA== | 46142.5913 | 2026-04-27 07:37 | Emailed Branch to close ticket | Completed | 2026-05-08 | WO-0560039 | Houston, TX | Dollar General #20582 | Houston | TX | 4967141 | FEXA | WATER LEAK & DOOR | DOOR REPLACEMENT - WARRANTY |  |  | RLN2MA/MY26B016475 |  | 3 units REG* RLN2MA- MY26B016476 Leaking. Tech MUST obtain Store Temperature & Humidity Readings. Take picture or write in ticket the CASE & CONDENSING UNIT equipment tag (model & serial #). o Store Hours: 8am – 9pm (store will not stay past closing) o Overtime Approved: NO o Problem: Check In/Out with Store Manager on Duty & Obtain Signature Hussmann R290 Microblock Equipment ONLY: RLN2MA- MY26B016476 Leaking. Tech can only work on multiple Hussmann R290 cases with one ticket, confirm all cases are operating or diagnose before leaving the store. • DO NOT work on existing cases, communicate to the Store MOD to place call with their service vendor. • Tech must list or take pictures of the data tag of all equipment model/serial number repaired on service ticket and provide a detail work summary of each equipment repaired. • If you need assistance, please contact the following Hussmann Technical Support Team @ 866-785-8499 or the following: 1) Todd Green @ 210-346-0005 2) Jeff Fosnaugh @ 314-501-8736 3) Andrew Miller @ 314-501-8698 • Hussmann Performance Parts @ 855-487-7778, option #3 – Warranty • Tecumseh compressor warranty – supply house will provide warranty tag to fill out & obtain a copy for office. Must purchase the compressor & file warranty claim. • If parts are not available & have long lead time, send an e-mail @ dg.service@hussmann.com to help locate. • Invoice MUST be submitted within 45 days of repair completion date to TAVANT. For support with warranty claim @ 800-398-7402, option #4 or hussmannwarrantyclaims@hussmann.com Send repair status with a brief work summary BEFORE leaving the location & contact to dg.service@hussmann.com. If you have any questions, contact us at @ dg.service@hussmann.com Troubleshooting Process Step 1 - Start with documentation located within case • Operation Manual & Data Sheet with the case. Step 2 - Scan Hussmann QR Code located on model/serial plate • Type serial number of case and follow navigation for product sheets, data sheets, and manuals Step 3 – Scan BOX QR Code for Box account • Carries in depth support - parameters, controller guides etc. Step 4 - Contact technical support - direct line #866-785-8499 • Tech support will escalate to our Field Equipment Team if issue cannot be resolved – tech support does not provide NTE/OT approval. Problem: MY26B014956 "Leaking Check In/Out with Store Manager on Duty & Obtain Signature Hussmann R290 Microblock Equipment ONLY: Model#: RLN3 Serial # MY26B014956 "Leaking Factory Order #: 901021 Ship Date: 2026-00-23 • TECH must obtain a photo of the equipment tag that includes MODEL & SERIAL number on the CASE & CONDENSING UNIT (Tecumseh) • Tech can only work on multiple Hussmann R290 cases with one ticket, confirm all cases are operating or diagnose before leaving the store. • DO NOT work on existing cases, communicate to the Store MOD to place call with their service vendor. • Tech must list or take pictures of the data tag of all equipment model/serial number repaired on service ticket and provide a detail work summary of each equipment repaired. • If you need assistance, please contact the following Hussmann Technical Support Team @ 866-785-8499 or the following: 1) Todd Green @ 210-346-0005 2) Jeff Fosnaugh @ 314-501-8736 3) Andrew Miller @ 314-501-8698 • Hussmann Performance Parts @ 855-487-7778, option #3 – Warranty • Tecumseh compressor warranty – supply house will provide warranty tag to fill out & obtain a copy for office. Must purchase the compressor & file warranty claim. • If parts are not available & have long lead time, send an e-mail @ dg.service@hussmann.com to help locate. • Invoice MUST be submitted within 45 days of repair completion date to TAVANT. For support with warranty claim @ 800-398-7402, option #4 or hussmannwarrantyclaims@hussmann.com Send repair status with a brief work summary BEFORE leaving the location & contact to dg.service@hussmann.com. If you have any questions, contact us at @ dg.service@hussmann.com Troubleshooting Process Step 1 - Start with documentation located within case • Operation Manual & Data Sheet with the case. Step 2 - Scan Hussmann QR Code located on model/serial plate • Type serial number of case and follow navigation for product sheets, data sheets, and manuals Step 3 – Scan BOX QR Code for Box account • Carries in depth support - parameters, controller guides etc. | 5/Helped tech Ray Rueda check out self contain cases leaking water , case kn back wall leaking water do to built up ice and gap between end panel and bottom of case bottom and case on side wall leaking water condensation down wall do to split insulation , reglued insulation and taped with insulation tape. ***Unable to check out of call*** 4/30Arrived onsite checked in with the store manager after talking withanager found case that were leaking had to use 6ft ladder to get on top of cases to checked drains and drain pans after looking at units found one unit to have a broke insulation on the suction line insulating was ripped had water build up and would run down the back wall onto the floore making big puddle of water so pulled back line fixed insulation with glue and insulation tape found other case to be leaking air on the outside that is leaking air from the inside blowing -10 defree air on outside panel causing it to sweat and make a ice ball on outsode of case all pucs are attached to wo will need to return with caulkinh and seal case properly were there will be no air escaping from unit causeing outsode to sweat and make water on floore will need to get with manager to see if install crew needs to return to properly seal case Resource: Ray Rueda
ec5d0a06-3442-f111-88b5-000d3a57f875 | 4sMxHfUJPecD40IcqEl9h9vp+HqORfRCwfUb/lezp2HGhQIKWh42QAJpyebo3nLCJQiXfKF5u9bLZDOGRGYFlw== | 46139.519 | 2026-04-27 05:25 |  | Completed | 2026-05-04 | WO-0559894 | RPM/Strategic Accounts | Dollar General #21342 | Klamath Falls | OR | TAVANT/PRODUCTCARE | STORE CONNECT | CASSETTE, UNDERCHARGE | REFRIGERANT |  |  | RLN3MA/MY26B016018, LEFT |  | Hussmann R290 Microblock Equipment ONLY: HIGH TEMPERATURE We are observing a High Temperature Alarm on the Serial number MY26B016018, RLN3MA, Left Microblock case at the above-mentioned location. The alarm has been active beyond the configured threshold of 60 minutes. | In regards to PO# TAVANT/ PRODUCT CARE Dollar General Store #21342 5927 S 6 th Street Klamath Falls Or 97603 (which is 1 1/2 hour drive from our location) Our tech got on site on 4/27/26 and found the left microblock condenser on the 3 door freezer was 20 deg higher than the right side. He contacted tech support and confirmed the unit was low on freon. R290. Tech support told him to weld in a service port so we could add refrigerant. Our tech did not have a service port at the time. We had to re schedule this call. On 5-1/26' our tech went on site and attached a service port to the pigtail on the compressor. He recovered existing refrigerant....pressure tested the system with magnets on both solenoid valves evacuated the system down to 454 microns and recharged the system with 100 grams of R290 refrigerant. The system was previously maintaining at 11Deg F and was at -4 deg and dropping in temp.
2ca1fee9-3e3f-f111-88b5-000d3a1d8d04 | hHujeJXLfj+DWeoZkHXT4K7txkk26WXJATdCAoYCxlFvO+DifBNuxSh4sWRHx0h1Q4l1qXlrSF9rrZebftg60Q== | 46135.8336 | 2026-04-23 11:05 |  | Completed | 2026-05-08 | WO-0558220 | Tulsa, OK | Dollar General #3294 | Galena | KS | 4854060 | FEXA | DISASTER MOVE CASES & MOVE BACK |  | X |  |  |  | 5/8 INSTALLED CASES, TRIMMED, WIRED, STARTED, SET CASES BACK IN ORIGINAL SPORT, REWIRED AND STARTED CASES BACK UP 5/5 MOVED CASES FOR WALL REPAIR
a6859881-173f-f111-88b5-000d3a1d8d04 | pwSG3VyyWWftTEAlHCbV+0MEjLZtljDk55u7Pj2tTfSJKnHMAP1bLE/hX2uIcDt1/W0/gj7tjNsqqnHoLQWURA== | 46135.6757 | 2026-04-23 06:23 |  | Completed | 2026-05-04 | WO-0557805 | RPM/Strategic Accounts | Dollar General #21130 | White City | OR | TAVANT/PRODUCTCARE | STORE CONNECT | COMMUNICATION |  |  |  | RLN3MA/MY26C019887 |  | MY26C019887 / RLN3MA Freezer 1 Communication Loss | 5/4 tech notes received regarding PO# 05557805 During the original installation of the units on the 2nd touch Dollar general remodel.Store # 21130 2399 Antelope Rd White City Or, 97503 We plugged in the condensers on the 3 door micro block freezer model I1RLN3MA Serial # MY26C019887 And the compressor started rattling like a can full of nails.....and the other one started to smoke. So we unhooked it. It turns out the electricians ran 220V to the plug.The model #s for these damaged condensers are Serial # 04C2426121074 Model # ALX44OU-DS3B01 and Serial # 04C2426121079 Model# ALX440U-DS3B01 Rob Starkey the project manager ordered new condensers and we installed them ASAP (once the electricians corrected the wiring) The #s for the new condensers are Serial # 04D1326121344 Model# ALX44OU-D53B01 And Serial# 04D1126121339 Model# ALX44OU-D53B01. Unfortunately when we installed the new condensers our tech that does the Gateway Networkand the network assets test was on a previously scheduled job out of the area. We did not have chance to get over the said site and get the units connected to the gateway until after you submitted work order PO#0557805. Rob Starkey said he would have the units we removed picked up.
c3c36211-4a3e-f111-88b5-000d3a1d8efd | NdAwUA9/cAtIZ8tcTurKKmV6FIQdNiraNVEKVTVMmNpU6wuZdRMJUx/ulPI7hkn8gN7Q+BYz5Dyzt2ADNh+1sQ== | 46142.1226 | 2026-04-22 05:52 |  | Completed | 2026-05-11 | WO-0557035 | Gulf | Dollar General #20876 | Elaine | AR | TAVANT/PRODUCTCARE | STORE CONNECT | COMMUNICATION | ` |  |  | RMN4MA/MY26B013850, RLN3MA/MY26B013819, RNL2MA/MY26B013812, RMN3MA/MY26B013772, RMN3MA/MY26B013770, RFMN5/MY19M090256, RFMN5/MY19M090255, RFLN4/MY19M090238, RFLN4/MY19M090237, RFLN3/MY19M090226 |  | Store Hours: 8am - 9pm (store personnel will not stay) OT APPROVED Priority: P1-Immediate Communication Loss It has been observed that the communication loss in below assets which generally results in uncontrolled temperatures, system shutdowns, and loss of automated data monitoring. Serial Number Customer Idetifiers ProductLine Model MY26B013850 4DR DRINK COOLER Microblock-Cases RMN4MA MY26B013819 3DR FROZEN FOOD 4 Microblock-Cases RLN3MA MY26B013812 2DR FROZEN FOOD 3 Microblock-Cases RLN2MA MY26B013772 3DR DAIRY/COOLER Microblock-Cases RMN3MA MY26B013770 3DR BEER COOLER Microblock-Cases RMN3MA MY19M090256 5DR DAIRY Freedomline RFMN5 MY19M090255 5DR DELI Freedomline RFMN5 MY19M090238 4DR FROZEN FOOD1 Freedomline RFLN4 MY19M090237 3 Freedomline RFLN4 MY19M090226 3DR ICE CREAM Freedomline RFLN3 The Tech team needs to visit the store and perform the following activities: Tech must obtain a photo of the equipment tag that includes Model & Serial Number on the case and Condensing Unit (Tecumseh). Please review and Confirm the Checklist items below: 1. Verify the Cases are connected to StoreConnect setup. Refer the attached gateway wiring document. 2. E2 shall not connect series to the cases. Verify E2 is connected to extension cable mentioned as From E2 in StoreConnect setup. Tech MUST contact Hussmann Connect Solutions via TEAMS when on site & before leaving the store: <insert names> • Tech can only work on multiple Hussmann R290 cases with one ticket, confirm all cases are operating or diagnose before leaving the store. • DO NOT work on existing cases, communicate to the Store MOD to place call with their service vendor. • Tech must list or take pictures of the data tag of all equipment model/serial number repaired on service ticket and provide a detail work summary of each equipment repaired. • If you need assistance, please contact the following Hussmann Technical Support Team @ 866-785-8499 or the following: 1) Todd Green @ 210-346-0005 2) Jeff Fosnaugh @ 314-501-8736 3) Andrew Miller @ 314-501-8698 • Hussmann Performance Parts @ 855-487-7778, option #3 – Warranty • Tecumseh compressor warranty – supply house will provide warranty tag to fill out & obtain a copy for office. Must purchase the compressor & file warranty claim. • If parts are not available & have long lead time, send an e-mail @ dg.service@hussmann.com to help locate. • Invoice MUST be submitted within 45 days of repair completion date to TAVANT. For support with warranty claim @ 800-398-7402, option #4 or hussmannwarrantyclaims@hussmann.com Send repair status with a brief work summary BEFORE leaving the location & contact to dg.service@hussmann.com. If you have any questions, contact us at @ dg.service@hussmann.com Troubleshooting Process Step 1 - Start with documentation located within case • Operation Manual & Data Sheet with the case. Step 2 - Scan Hussmann QR Code located on model/serial plate • Type serial number of case and follow navigation for product sheets, data sheets, and manuals Step 3 – Scan BOX QR Code for Box account • Carries in depth support - parameters, controller guides etc. Step 4 - Contact technical support - direct line #866-785-8499 • Tech support will escalate to our Field Equipment Team if issue cannot be resolved – tech support does not provide NTE/OT approval. | 5/11/26 Tech: kris clark Arrived onsite and checked in. Most freezer doors old and new were sweating at arrival. All antisweat controllers were working and cycling. The store humidity at best was 58% with a store temperature of 72. The site humidity needs to be addressed by the primary service provider. I installed a flashing on the endcap to stop the hot discharge air from hitting our case. Job is complete. 4/22/26 Tech: kris clark Hussmann beverage cooler model: RMN4MA Serial: MY26B013850 Arrived onsite to find all cases offline on store connect but the humidity sensor was online. i verified this was accurate in the gateway. I found that there was a bad wire connection from the store connect equiment to the comm.line for the cases. I also found they had tied in the store connect into the comm.line as a star ( 3 comm.lines tie together) versus the required daisy chain, i corrected this issue by pulling one of the comm.lines out of the junction and running it to the other controller to create the proper daisy chain. All systems came back online in the gateway and store connect. the job is complete Resource: Kristopher Clark
350d8c77-a23d-f111-88b5-7c1e5257c108 | KSFFwowSnqALnT9CmK/6qclRSVY2eWheE0vSeXTb/rj1eYoICMNdoT4mLIRigvAswPWdW/67F0MOpMYJXyy36g== | 46139.6859 | 2026-04-21 09:53 |  | Completed | 2026-05-21 | WO-0556537 | Dallas, TX | Dollar General #22930 | Forestburg | TX | 4952759 | FEXA | TEMPERATURE | PRODUCT LOSS - 4 LT, ICE CREAM |  |  | RLN4MA/MY26B014974 | YES | Below are the details for a new service call. o Site Name/#: Dollar General # 22930 o Address: 16621 FM 455 Forestburg TX 76239 o Store Hours: 8am – 9pm (store will not stay past closing) o Overtime NO o PO: 4952759 o Problem: Check In/Out with Store Manager on Duty & Obtain Signature Hussmann R290 Microblock Equipment ONLY: RLN4MA- MY26B014974 Ice cream is melting/other product is damaged Tech must obtain a photo of the equipment tag that includes Model & Serial Number on the case and Condensing Unit (Tecumseh). Please review and Confirm the Checklist items below. Tech MUST contact Hussmann Connect Solutions via TEAMS when on site & before leaving the store: <insert names> • Tech can only work on multiple Hussmann R290 cases with one ticket, confirm all cases are operating or diagnose before leaving the store. • DO NOT work on existing cases, communicate to the Store MOD to place call with their service vendor. • Tech must list or take pictures of the data tag of all equipment model/serial number repaired on service ticket and provide a detail work summary of each equipment repaired. • If you need assistance, please contact the following Hussmann Technical Support Team @ 866-785-8499 or the following: 1) Todd Green @ 210-346-0005 2) Jeff Fosnaugh @ 314-501-8736 3) Andrew Miller @ 314-501-8698 • Hussmann Performance Parts @ 855-487-7778, option #3 – Warranty • Tecumseh compressor warranty – supply house will provide warranty tag to fill out & obtain a copy for office. Must purchase the compressor & file warranty claim. • If parts are not available & have long lead time, send an e-mail @ dg.service@hussmann.com to help locate. • Invoice MUST be submitted within 45 days of repair completion date to TAVANT. For support with warranty claim @ 800-398-7402, option #4 or hussmannwarrantyclaims@hussmann.com Send repair status with a brief work summary BEFORE leaving the location & contact to dg.service@hussmann.com. If you have any questions, contact us at @ dg.service@hussmann.com Troubleshooting Process Step 1 - Start with documentation located within case • Operation Manual & Data Sheet with the case. Step 2 - Scan Hussmann QR Code located on model/serial plate • Type serial number of case and follow navigation for product sheets, data sheets, and manuals Step 3 – Scan BOX QR Code for Box account • Carries in depth support - parameters, controller guides etc. Step 4 - Contact technical support - direct line #866-785-8499 • Tech support will escalate to our Field Equipment Team if issue cannot be resolved – tech support does not provide NTE/OT approval. | 05/20/26 went to united and picked up some r-290 and went to the shop and disassemble the whole skid and took out the bad txv and welded in and installed the new one and pulled a deep vacuum and recharged the system with the factory charge of 100grams of r-290 once that was done i reassembled the whole skid and got it ready to be installed Trevor is having one of the warehouse employees deliver the unit to the store tomorrow to help me install it. 05/21/26 upon arrival I checked in with the manager on duty after checking in i waited for the warhouse guy to arrived with the unit we unloaded it and got it on top of the case and after doing so i hooked everything up and wired it back in and turned the 2 units back on for the case and waited for both of them to get to the temperature setpoint of 9.9 degrees see attached photos of the controller for both units both skids are getting to temp watched them both cycle multiple times case is working properly I then tested defrost on both skids for the case and both are working properly waited for care to get back down to temp and cleaned up any mess that was made and put the case trim back together job complete Pictures attached. Upon arrival i found case in question no running cold enough for ice cream . The microblock unit on the left was running 9 degrees. The one on the left running -2 . After checking amp draw ect i had correct charge issues on other cases in this store i evacuated system pulled vac and charged system with scale. I let it run for quite a while but it pulled down and started flooding back. I called hussmann tech support and waited for a long time with no response after i was able to talk to them they recommend turning off unit and letting it defrost overnight so if ice is on coil it would defrost. I had to wait until store could pull product. I turned off both units. I returned 4-23 started up both units i also found sections where penatrations was not sealedi aded pics i used foam and sealed like the other cases in the store is. I also found screws missing on coil box i added them as needed. I gave compressors plenty of time to reach temp the coil on the right never reached temp and is flooding back. I called tech support again and they called back several times after this we came to the conclusion that txv is bad and needs to be changed but we can not access that so new skid will be sent to store and old one returned and repaired. Resource: Chris Boatner
19268819-be3c-f111-88b5-7c1e5257c108 | CXvh8Gp7hq6og6Yaz0J+GyRQVx4cRCV+WKmyCA+5K+MTy8OBOO28n26+DdPCC6KFdlzdOJDq54ar8a57jfdFIQ== | 46140.5963 | 2026-04-20 06:38 |  | Completed | 2026-04-22 13:02 | WO-0555457 | Charlotte, NC | Dollar General #6099 | Newton | NC | 4942182 | FEXA | POWER |  | X |  | RMN4MA/MY26B016530 | YES | Below are the details for a new service call. o Site Name/#: Dollar General 6099 o Address: 3867 Startown Rd Newton NC 28658 o Store Hours: 8am – 9pm (store will not stay past closing) o Overtime NO o PO: 0555457 o Problem: Check In/Out with Store Manager on Duty & Obtain Signature Hussmann R290 Microblock Equipment ONLY: RMN4MA-MY26B016530- No power Tech must obtain a photo of the equipment tag that includes Model & Serial Number on the case and Condensing Unit (Tecumseh). Please review and Confirm the Checklist items below. Tech MUST contact Hussmann Connect Solutions via TEAMS when on site & before leaving the store: <insert names> • Tech can only work on multiple Hussmann R290 cases with one ticket, confirm all cases are operating or diagnose before leaving the store. • DO NOT work on existing cases, communicate to the Store MOD to place call with their service vendor. • Tech must list or take pictures of the data tag of all equipment model/serial number repaired on service ticket and provide a detail work summary of each equipment repaired. • If you need assistance, please contact the following Hussmann Technical Support Team @ 866-785-8499 or the following: 1) Todd Green @ 210-346-0005 2) Jeff Fosnaugh @ 314-501-8736 3) Andrew Miller @ 314-501-8698 • Hussmann Performance Parts @ 855-487-7778, option #3 – Warranty • Tecumseh compressor warranty – supply house will provide warranty tag to fill out & obtain a copy for office. Must purchase the compressor & file warranty claim. • If parts are not available & have long lead time, send an e-mail @ dg.service@hussmann.com to help locate. • Invoice MUST be submitted within 45 days of repair completion date to TAVANT. For support with warranty claim @ 800-398-7402, option #4 or hussmannwarrantyclaims@hussmann.com Send repair status with a brief work summary BEFORE leaving the location & contact to dg.service@hussmann.com. If you have any questions, contact us at @ dg.service@hussmann.com Troubleshooting Process Step 1 - Start with documentation located within case • Operation Manual & Data Sheet with the case. Step 2 - Scan Hussmann QR Code located on model/serial plate • Type serial number of case and follow navigation for product sheets, data sheets, and manuals Step 3 – Scan BOX QR Code for Box account • Carries in depth support - parameters, controller guides etc. Step 4 - Contact technical support - direct line #866-785-8499 • Tech support will escalate to our Field Equipment Team if issue cannot be resolved – tech support does not provide NTE/OT approval. | 04/22/2026 BD. Verified that hussmann cases have power and are operating at this time I also spoke with James Mcdaniel about any other issues at this location. Resource: Brian Davis completed Resource: Brian Davis
a0e11234-403b-f111-88b5-7c1e5257c77a | BpY2Qo1i9xHkaDWr0WHTcHFaQRi/XQ4cjtGcRz1url7JGnOOXSDBe/tE/kfQl9E8lmk6rktHbkyx95e/TDhzfA== | 46135.5754 | 2026-04-18 09:04 |  | Completed | 2026-04-18 10:00 | WO-0554820 | RPM/Strategic Accounts | Dollar General #22982 | Ropesville | TX | TAVANT/PRODUCTCARE | STORE CONNECT | TEMPERATURE |  |  |  | RLN4MA/MY26B014967, LEFT |  | Response : Priority: P1-Immediate Job Scope: HIGH TEMPERATURE We are observing a High Temperature Alarm on the Serial number MY26B014967, RLN4MA, Left & Center/Right Microblock case at the above-mentioned location. The alarm has been active beyond the configured threshold of 60 minutes. Tech must obtain a photo of the equipment tag that includes Model & Serial Number on the case and Condensing Unit (Tecumseh). Please review and Confirm the Checklist items below: The store is currently operational and fully stocked with products. If this condition is not addressed immediately, it may result in product loss, food safety risk, and significant store operational impact, potentially leading to customer dissatisfaction. To prevent any product loss and ensure continued store operations, we request an immediate P1 (Critical) level site visit. Checklist: • Inspect the evaporator coil for ice or frost accumulation • Verify the evaporator fan is active and running properly • Confirm airflow direction and un-obstructed air circulation • If ice is present: Perform a manual defrost to fully clear the evaporator coil • Verify Hot Gas Valve operation during defrosts • Confirm the condenser fan turns OFF during defrost • Verify the refrigerant charge level • If low, charge the system to the manufacturer-recommended level | Rene spoke with the store manager Paul on 4/20 and was informed that everything was working. Resource: CLIMATE COOL LLC
577fface-bf39-f111-88b5-7c1e5257c108 | sRaLO4eGLcRGcCtodrxUqBk2Vi27x2tYNEcpe+aHB9o5kaqurYV0RHcn7HXNwMXeUqqM2IOuFAtJEQQ0Yzg/AA== | 46138.9399 | 2026-04-16 11:12 | No Updates Found | Completed | 2026-05-27 | WO-0553563 | Kansas City, MO (Lenexa) | Dollar General | Bridgeton | MO | TIM SMITH/SMALL FORMAT SALES | TIM SMITH | CASE TRIM |  | X |  |  |  | Tech to arrive at the Hussmann Corporate Office on Tuesday, April 21st @ 8am; contact Andrew Miller/Project Manager @ 314-683-6676 or Erin Moran/SAR @ 314-380-3479 Set cases, install trim, facia & miscellaneous case parts. Contact: Andrew Miller/Project Manager @ 314-683-6676
6740b263-bd39-f111-88b5-000d3a57f5f2 | vg+A7ydqKjqDySMdIStqHufkXmUgelQy6LwZ6BLZ/7NJrb1s6u4odt9pOCDsrk8gFK0cKwoIJsmERTmNB0yrbQ== | 46139.52 | 2026-04-16 10:55 | 6/2 Parts have been ordered 5/19 Warranty not covering - ordering through PP 4/30 Warranty door replacement - Suzanne sent email - waiting on response | Parts Needed |  | WO-0553537 | Houston, TX | Dollar General #21135 | La Marque | TX | 4934816 | FEXA | WATER LEAK |  |  |  | RMN3MA/MY26b016480 | YES | REG* rmn3ma, my26b016480, Water is leaking under unit unit is leaking lots of water, cant tell which unit its coming from- will put in another ticket in case its coming from the other one Hussmann Cases ONLY: rmn3ma, my26b016480, Water is leaking under unit unit is leaking lots of water, cant tell which unit its coming from- will put in another ticket in case its coming from the other one STORES BUSINESS HOURS: 8am – 9pm (store will not stay past closing) Check In/Out with Store Manager on Duty, OBTAIN A SIGNATURE ON SERVICE TICKET & NOTE FIRST AND LAST NAME. Tech can work on multiple Hussmann Cases with one ticket, confirm all cases are operating or diagnose before leaving the store. Tech must list or take pictures of the data tag of all equipment model/serial number repaired on service ticket and provide a detail work summary of each equipment repaired. If you need assistance, please contact Hussmann Technical Support @ 800-922-1919, option #3. If Parts are needed, contact Hussmann Performance Parts @ 855-487-7778, press 1 for general inquiries. Confirm Copeland compressors are under warranty over the counter through United or Copeland Distributor. Sanhua TXV replacement is not available – source Sporlan. If parts are not available & have long lead time, send us an e-mail @ dg.service@hussmann.com to help locate. Invoice MUST be submitted within 30 days from date of repair completion to April Marolf @ april.marolf@hussmann.com and dg.service@hussmann.com. Send repair status with a brief work summary BEFORE leaving the location to dg.service@hussmann.com. If you have any questions, contact us at @ dg.service@hussmann.com | rerouted Resource: Julio Padilla 4/20/26 RCortez - Arrived on site. Checked in with manager. Checked case and found large amount of water on shelving and under case panels. Removed panels to uncover evap section. Found water leaking from drain tube outlet side. Found tape blocking end of tube and condenser fan motor wiring tucked underneath drain tube propping up end of tube and not allowing water to flow. Corrected wire run on fan motor to run over drain instead of under. Removed tape from end of tube to allow flow. Vacuumed water from under case. Found first door on case not closing automatically. Found door rod to be broken inside door. Will most likely need new door or door rod to resolve issue. Spoke with Ellen Decker before leaving. Resource: Raymond Cortez
efe8a26f-d938-f111-88b4-7c1e52ff753b | OlEKpkF3EhOrrqDieLfcQcLc5/bQbsM0BxTN4WUTC2StGTS3yiCqBDCiQwIbxX5s2/gr3EYlenK/1XV8FJeI+w== | 46139.9391 | 2026-04-15 07:43 |  | Posted | 2026-04-15 15:03 | WO-0552572 | Gulf | Dollar General #21377 | Starkville | MS | TAVANT/PRODUCT CARE | FEXA | ICE/FROST |  |  |  | RLN2MA/MY26B013804, LEFT |  | Below are the details for a new service call. o Site Name/#: Dollar General 21377 o Address: 1818 South Montgomery Street, Starkville, MS, USA, 39759 o Store Hours: 8am – 9pm (store will not stay past closing) o Overtime Priority: P1-Immediate o PO: 0552572 o Problem: Check In/Out with Store Manager on Duty & HIGH TEMPERATURE Obtain Signature Hussmann R290 Microblock Equipment ONLY: Tech must obtain a photo of the equipment tag that includes Model & Serial Number on the case and Condensing Unit (Tecumseh). Please review and Confirm the Checklist items below. We are observing a High Temperature Alarm on the Serial number MY26B013804, RLN2MA, Left Microblock case at the above-mentioned location. The alarm has been active beyond the configured threshold of 60 minutes. The store is currently operational and fully stocked with products. If this condition is not addressed immediately, it may result in product loss, food safety risk, and significant store operational impact, potentially leading to customer dissatisfaction. To prevent any product loss and ensure continued store operations, we request an immediate P1 (Critical) level site visit. Checklist: • Inspect the evaporator coil for ice or frost accumulation • Verify the evaporator fan is active and running properly • Confirm airflow direction and un-obstructed air circulation • If ice is present: Perform a manual defrost to fully clear the evaporator coil • Verify Hot Gas Valve operation during defrosts • Confirm the condenser fan turns OFF during defrost • Verify the refrigerant charge level • If low, charge the system to the manufacturer-recommended level Tech must obtain a photo of the equipment tag that includes Model & Serial Number on the case and Condensing Unit (Tecumseh). Please review and Confirm the Checklist items below. Tech MUST contact Hussmann Connect Solutions via TEAMS when on site & before leaving the store: <insert names> • Tech can only work on multiple Hussmann R290 cases with one ticket, confirm all cases are operating or diagnose before leaving the store. • DO NOT work on existing cases, communicate to the Store MOD to place call with their service vendor. • Tech must list or take pictures of the data tag of all equipment model/serial number repaired on service ticket and provide a detail work summary of each equipment repaired. • If you need assistance, please contact the following Hussmann Technical Support Team @ 866-785-8499 or the following: 1) Todd Green @ 210-346-0005 2) Jeff Fosnaugh @ 314-501-8736 3) Andrew Miller @ 314-501-8698 • Hussmann Performance Parts @ 855-487-7778, option #3 – Warranty • Tecumseh compressor warranty – supply house will provide warranty tag to fill out & obtain a copy for office. Must purchase the compressor & file warranty claim. • If parts are not available & have long lead time, send an e-mail @ dg.service@hussmann.com to help locate. • Invoice MUST be submitted within 45 days of repair completion date to TAVANT. For support with warranty claim @ 800-398-7402, option #4 or hussmannwarrantyclaims@hussmann.com Send repair status with a brief work summary BEFORE leaving the location & contact to dg.service@hussmann.com. If you have any questions, contact us at @ dg.service@hussmann.com Troubleshooting Process Step 1 - Start with documentation located within case • Operation Manual & Data Sheet with the case. Step 2 - Scan Hussmann QR Code located on model/serial plate • Type serial number of case and follow navigation for product sheets, data sheets, and manuals Step 3 – Scan BOX QR Code for Box account • Carries in depth support - parameters, controller guides etc. Step 4 - Contact technical support - direct line #866-785-8499 • Tech support will escalate to our Field Equipment Team if issue cannot be resolved – tech support does not provide NTE/OT approval.
0855b5b8-ca38-f111-88b5-000d3a57f0ee | qKBWNhkg28JKT7rS4/sDVGlMef61CI9uYuwFQhmSObXtvDcioSTAy8egwCpl2StmJ7CIW5gNb/jYIz5tXUkIVg== | 46135.6267 | 2026-04-15 05:58 |  | Completed | 2026-04-15 16:13 | WO-0552473 | Dallas, TX | Dollar General #22930 | Forestburg | TX | TAVANT/BR INSTALLATION | TAVANT/BRANCH - RICHARD JOHNSON/INSTALLTION | REFRIGERANT LEAK |  |  |  | RMN3MA/MY26C025316 | YES | Hussmann M#RMN3MA S#MY26C025316 possibly has no charge on the two micro blocks. | I found one system with leak on drier i added video of leak . I repaired leak pulled vac and added r290 100 gm. The other system i couldnt find a leak but system would not pull down . I evacuated system pulled vac and weighed in chargecas needed r290 started ul case came down to temp. I removed access fittings and sealed both systems. Resource: Chris Boatner
20721187-4038-f111-88b5-000d3a1d8091 | 4S3+E7S61Ao4/1gv5nVL+g65pcxXi2cIYTUTDjVKdbSdTWP90t4FK1XzAR/XFSOF0DIIB1ahjWBkYWM2Rf8mPQ== | 46140.6723 | 2026-04-14 13:29 |  | Completed | 2026-04-21 20:47 | WO-0552129 | Houston, TX | Dollar General #14858 | Houston | TX | TAVANT/PRODUCT CARE | STORE CONNECT | ICE/FROST |  |  |  | RLN3MA/MY26B016004 | YES | REG* It has been observed that the High superheat is causing unit to not pull down in the refrigeration unit, which may impact cooling efficiency, increase compressor load, lead to higher energy consumption, and risk improper temperature control of stored products.” Below are the details for a new service call. o Site Name/#: Dollar General 14858 o Address: 4750 W Fuqua St, Houston, Texas, 77053. o Store Hours: 8am – 9pm (store will not stay past closing) o P2 – Medium (24-28 Hours) o PO: WO-0552129 o Problem: Check In/Out with Store Manager on Duty & Obtain Signature Hussmann R290 Microblock Equipment ONLY: Serial # MY26B016004 – Lack of Refrigerant Tech must obtain a photo of the equipment tag that includes Model & Serial Number on the case and Condensing Unit (Tecumseh). Please review and Confirm the Checklist items below. It has been observed that the High superheat is causing unit to not pull down in the refrigeration unit, which may impact cooling efficiency, increase compressor load, lead to higher energy consumption, and risk improper temperature control of stored products.” Asset Details: Productline Serial Number Module Assets Model Alt Name Microblock MY26B016004 Left RLN3MA FROZEN FOOD The asset is currently operational and fully stocked with products. If this condition is not addressed immediately, it may result in product loss, food safety risk, and significant store operational impact, potentially leading to customer dissatisfaction. To prevent any product loss and ensure continued store operations, we request an P2 – Medium (24-28 Hours) level site visit. Checklist: • Verify the refrigerant charge level • If low, charge the system to the manufacturer-recommended level • Verify the TXV Setting • Inspect the evaporator coil for ice or frost accumulation • Verify the evaporator fan is active and running properly • Confirm airflow direction and un-obstructed air circulation • If ice is present: Perform a manual defrost to fully clear the evaporator coil • Verify Hot Gas Valve operation during defrosts • Confirm the condenser fan turns OFF during defrost • Tech can only work on multiple Hussmann R290 cases with one ticket, confirm all cases are operating or diagnose before leaving the store. • DO NOT work on existing cases, communicate to the Store MOD to place call with their service vendor. • Tech must list or take pictures of the data tag of all equipment model/serial number repaired on service ticket and provide a detail work summary of each equipment repaired. • If you need assistance, please contact the following Hussmann Technical Support Team @ 866-785-8499 or the following: 1) Todd Green @ 210-346-0005 2) Jeff Fosnaugh @ 314-501-8736 3) Andrew Miller @ 314-501-8698 • Hussmann Performance Parts @ 855-487-7778, option #3 – Warranty • Tecumseh compressor warranty – supply house will provide warranty tag to fill out & obtain a copy for office. Must purchase the compressor & file warranty claim. • If parts are not available & have long lead time, send an e-mail @ dg.service@hussmann.com to help locate. • Invoice MUST be submitted within 45 days of repair completion date to TAVANT. For support with warranty claim @ 800-398-7402, option #4 or hussmannwarrantyclaims@hussmann.com Send repair status with a brief work summary BEFORE leaving the location & contact to dg.service@hussmann.com. If you have any questions, contact us at @ dg.service@hussmann.com Troubleshooting Process Step 1 - Start with documentation located within case • Operation Manual & Data Sheet with the case. Step 2 - Scan Hussmann QR Code located on model/serial plate • Type serial number of case and follow navigation for product sheets, data sheets, and manuals Step 3 – Scan BOX QR Code for Box account • Carries in depth support - parameters, controller guides etc. Step 4 - Contact technical support - direct line #866-785-8499 • Tech support will escalate to our Field Equipment Team if issue cannot be resolved – tech support does not provide NTE/OT approval. | Dollar general #14858 Hussmann case Mn-RLN3MA SN-MY26B016004 UPON ARRIVAL FOUND CASE OUT V OF TEMP SOME ICE BUILD UP PLACED IN DEFROST, STARTED TO TROUBLE SHOOT HOWEVER PRESSURES ARE REQUIRED AND THIS IS A R290 CASE, WHICH I DO NOT HAVE THE EQUIPMENT REQUIRED TO CHECK THIS UNIT AT MONEMT, RECHEAHED OUT TO DISPATCH, ANOTHER TECH WILL BE DISPATCHED OUT Resource: Julio Padilla Arrived on site checked in with manager. Found case that was on work order and checked operation. Found ice coming from discharge air side of microblock. Looks to be coming for the block seal or drain line. Also got with tech support to go over the check list. Found conflicting wire diagrams on unit the diagram shows condenser wired in with compressor. On hussmann manual and PDF manual that tech support send out condenser fan looks to be two speed motor wired into board point NO4. Also controller has board point NO4 Associated to condenser fan motor. Ran case through couple defrost to ensure coil was clear and airflow was not an issue. Talk to rigoberto Guzman hussmann engineer and did not confirm which one is correct hussmann manual has a revised date of February 2026. Amp drawed compressors on both micro blocks the one with issue is showing one amp less than the one reaching said point indicating possible leak. Sprayed bubbles on several connections and did not find leak at this time. Will return tomorrow with propane leak detector and smoke machine to locate leaks. Will also need propane scale and gas to make repair. Checked out with manager work order complete Resource: Marcelino Garcia Went to shop picked up propane or 290 scale and r290 leak detector. Stopped at supply house picked up bottle of r290 piercing valves and access fittings. Return to store and checked in with the manager. Leak checked unit condenser evaporator compressors and all solder connections could not find leak. Installed piercing valves to verify pressure and unit may be low on charge. Evacuated unit installed installed access fittings and use proper nitrogen flowing procedures. Pressured up system to 200 lb and used digital gauge to conduct tightness test. Ran test for 30 minutes and pressure was not dropping. Evaporator compartment cover to inspect for air penetration leak. Found two spots that could be an issues where butyl caulk was not applied. Where the liquid and hot gas line penetrate through the trough moisture is present. Used 1/8 inch by 2 in insulation tape and ran tape along bottom of evaporator compartment enclosure to help seal enclosure. Laid extra piece wear penetrations come in to help fill Gap. Putting closure back together and pulled vacuum on condensing unit. Got vacuumed down to microns and charge unit with 101 G of r290 refrigerant. Started up unit and pressures and drop rate on temperature are looking good. Unit performed well after repair and compressor is cycling on temperature as designed. Ran smoke machine through inside of case to locate any other air leak penetration and also to verify it evaporator compartment repair. Found doors are leaking at top of case where seal meets contact plate. Doors will need to be adjusted to fix the issue. Will request a non mechanical technician to come and adjust doors and seal wire penetration further with foam. Checked out with manager and informed her of situation with case. Case is at temp and maintaining will leave work order pause to complete repair. Resource: Marcelino Garcia I arrived and checked in with the store manager, then proceeded to inspect the system that had been reported to me. I found that it was functioning properly, so I verified that the compressor was starting up and engaging based on temperature. Since everything is working correctly, this work order is now complete. Resource: Yelson Canadas Assisted tech with new install cases running warm. Used foam and butyle to reseal self contained system Resource: Jaime Hinojosa Arrived outside checked in with manager and proceeded to leak check case again. Found no leaks with detector detek Stratus. After reviewing graphs seems to have evaporator iced up. Ran cased through several defrost to ensure coil was clear. Attempted to adjust doors and heated gaskets to prevent air leak. Will need non mechanical check out to take a look at doors. Gets down to -5° and is struggling to get to set point. After all is equal on both compressors and two door case next to four-door is alarming as well high temp. No further work can be done on with refrigeration system at this time. Checked out with manager Resource: Marcelino Garcia
1dc25de9-3f38-f111-88b5-000d3a1d8091 | 5mPZ9DZ1cbX04ydwXZlOLYZtv7JHDC4CT7HlmrUy8C6Kvyix+5RipRKhBRrQPmqDtkFQ9ibNNqHEkx6NgRD5pg== | 46135.0073 | 2026-04-14 13:24 |  | Completed | 2026-04-16 16:19 | WO-0552123 | Phoenix, AZ | Dollar General #22613 | Hereford | AZ | TAVANT/PRODUCT CARE | STORE CONNECT | WIRING |  |  |  | RLN2MA/MY26B014941 |  | Below are the details for a new service call. o Site Name/#: Dollar General 22613 o Address: 9527 E HIGHWAY 92, HEREFORD, AZ, 85615 o Store Hours: 8am – 9pm (store will not stay past closing) o P2 – Medium (24-28 Hours) o PO: WO-0552123 o Problem: Check In/Out with Store Manager on Duty & Obtain Signature Hussmann R290 Microblock Equipment ONLY: Serial # MY26B014941 – Lack of Refrigerant Tech must obtain a photo of the equipment tag that includes Model & Serial Number on the case and Condensing Unit (Tecumseh). Please review and Confirm the Checklist items below. It has been observed that the High superheat is causing unit to not pull down in the refrigeration unit, which may impact cooling efficiency, increase compressor load, lead to higher energy consumption, and risk improper temperature control of stored products.” Asset Details: Productline Serial Number Module Assets Model Alt Name Microblock MY26B014941 Left RLN2MA Freezer-1 The asset is currently operational and fully stocked with products. If this condition is not addressed immediately, it may result in product loss, food safety risk, and significant store operational impact, potentially leading to customer dissatisfaction. To prevent any product loss and ensure continued store operations, we request an P2 – Medium (24-28 Hours) level site visit. Checklist: • Verify the refrigerant charge level • If low, charge the system to the manufacturer-recommended level • Verify the TXV Setting • Inspect the evaporator coil for ice or frost accumulation • Verify the evaporator fan is active and running properly • Confirm airflow direction and un-obstructed air circulation • If ice is present: Perform a manual defrost to fully clear the evaporator coil • Verify Hot Gas Valve operation during defrosts • Confirm the condenser fan turns OFF during defrost • Tech can only work on multiple Hussmann R290 cases with one ticket, confirm all cases are operating or diagnose before leaving the store. • DO NOT work on existing cases, communicate to the Store MOD to place call with their service vendor. • Tech must list or take pictures of the data tag of all equipment model/serial number repaired on service ticket and provide a detail work summary of each equipment repaired. • If you need assistance, please contact the following Hussmann Technical Support Team @ 866-785-8499 or the following: 1) Todd Green @ 210-346-0005 2) Jeff Fosnaugh @ 314-501-8736 3) Andrew Miller @ 314-501-8698 • Hussmann Performance Parts @ 855-487-7778, option #3 – Warranty • Tecumseh compressor warranty – supply house will provide warranty tag to fill out & obtain a copy for office. Must purchase the compressor & file warranty claim. • If parts are not available & have long lead time, send an e-mail @ dg.service@hussmann.com to help locate. • Invoice MUST be submitted within 45 days of repair completion date to TAVANT. For support with warranty claim @ 800-398-7402, option #4 or hussmannwarrantyclaims@hussmann.com Send repair status with a brief work summary BEFORE leaving the location & contact to dg.service@hussmann.com. If you have any questions, contact us at @ dg.service@hussmann.com Troubleshooting Process Step 1 - Start with documentation located within case • Operation Manual & Data Sheet with the case. Step 2 - Scan Hussmann QR Code located on model/serial plate • Type serial number of case and follow navigation for product sheets, data sheets, and manuals Step 3 – Scan BOX QR Code for Box account • Carries in depth support - parameters, controller guides etc. Step 4 - Contact technical support - direct line #866-785-8499 • Tech support will escalate to our Field Equipment Team if issue cannot be resolved – tech support does not provide NTE/OT approval. | Arrived to the store, made contact with the management, found case was at 2.8⁰, found the case had low air flow, found that one of the fans was not making a connection in the Phoenix connector, found the Phoenix connector was pinching on the wires insulation. I disconnected the wire, stripped the wire back, reconnected the wire, checked the fans running amps (0.2 amps), and allowed the case to drop into the negatives. Resource: Erich McGhee Arrived to the store, made contact with the management, found case was at 2.8⁰, found the case had low air flow, found that one of the fans was not making a connection in the Phoenix connector, found the Phoenix connector was pinching on the wires insulation. I disconnected the wire, stripped the wire back, reconnected the wire, checked the fans running amps (0.2 amps), and allowed the case to drop into the negatives. Resource: Erich McGhee
e47e2975-3c38-f111-88b5-000d3a1d8091 | B2f5IQqv8FNKCmFr5Uimp2NNkyI0nLtvffv38hLoDxxsTX5UpvGSARXognMKU0d/cKpSKgpScFBjHHR/p763Yw== | 46135.0107 | 2026-04-14 13:00 |  | Completed | 2026-04-15 06:00 | WO-0552093 | RPM/Strategic Accounts | Dollar General #3270 | San Angelo | TX | TAVANT/PRODUCTCARE | STORE CONNECT | REFRIGERANT |  |  |  | RLN3MA/MY26B016488, RIGHT | YES | Below are the details for a new service call. o Site Name/#: Dollar General o Address: 2934 N Chadbourne St, San Angelo, Texas, 76903 o Store Hours: 8am – 9pm (store will not stay past closing) o P2 – Medium (24-28 Hours) o PO: WO-0552093 o Problem: Check In/Out with Store Manager on Duty & Obtain Signature Hussmann R290 Microblock Equipment ONLY: Serial # MY26B016488 - Lack of Refrigerant Asset Details: Productline Serial Number Module Assets Model Alt Name Microblock MY26B016488 Center/ Right RLN3MA Frozen food 4 The asset is currently operational and fully stocked with products. If this condition is not addressed immediately, it may result in product loss, food safety risk, and significant store operational impact, potentially leading to customer dissatisfaction. To prevent any product loss and ensure continued store operations, we request an P2 – Medium (24-28 Hours) level site visit. Checklist: • Verify the refrigerant charge level • If low, charge the system to the manufacturer-recommended level • Verify the TXV Setting • Inspect the evaporator coil for ice or frost accumulation • Verify the evaporator fan is active and running properly • Confirm airflow direction and un-obstructed air circulation • If ice is present: Perform a manual defrost to fully clear the evaporator coil • Verify Hot Gas Valve operation during defrosts • Confirm the condenser fan turns OFF during defrost • Tech can only work on multiple Hussmann R290 cases with one ticket, confirm all cases are operating or diagnose before leaving the store. • DO NOT work on existing cases, communicate to the Store MOD to place call with their service vendor. • Tech must list or take pictures of the data tag of all equipment model/serial number repaired on service ticket and provide a detail work summary of each equipment repaired. • If you need assistance, please contact the following Hussmann Technical Support Team @ 866-785-8499 or the following: 1) Todd Green @ 210-346-0005 2) Jeff Fosnaugh @ 314-501-8736 3) Andrew Miller @ 314-501-8698 • Hussmann Performance Parts @ 855-487-7778, option #3 – Warranty • Tecumseh compressor warranty – supply house will provide warranty tag to fill out & obtain a copy for office. Must purchase the compressor & file warranty claim. • If parts are not available & have long lead time, send an e-mail @ dg.service@hussmann.com to help locate. • Invoice MUST be submitted within 45 days of repair completion date to TAVANT. For support with warranty claim @ 800-398-7402, option #4 or hussmannwarrantyclaims@hussmann.com Send repair status with a brief work summary BEFORE leaving the location & contact to dg.service@hussmann.com. If you have any questions, contact us at @ dg.service@hussmann.com Troubleshooting Process Step 1 - Start with documentation located within case • Operation Manual & Data Sheet with the case. Step 2 - Scan Hussmann QR Code located on model/serial plate • Type serial number of case and follow navigation for product sheets, data sheets, and manuals Step 3 – Scan BOX QR Code for Box account • Carries in depth support - parameters, controller guides etc. Step 4 - Contact technical support - direct line #866-785-8499 • Tech support will escalate to our Field Equipment Team if issue cannot be resolved – tech support does not provide NTE/OT approval. | REFERENCE BUDIK'S EMAIL: 4/20 Encore confirmed call completed Resource: ENCORE MECHANICAL LLC
a7d47a14-3b38-f111-88b5-000d3a1d8091 | ug6gdmJs5dg2G4VnJT4Ln5Kuz9c08NFWtUT2YFeoszt17AJ9jKQAmx9AlDmXiETNIeaqnYUuPA7vS5w18HY23A== | 46132.6614 | 2026-04-14 12:50 |  | Completed | 2026-04-15 06:00 | WO-0552080 | RPM/Strategic Accounts | Dollar General #22281 | Hamlet | IN | TAVANT/PRODUCT CARE | STORE CONNECT | NUISANCE |  |  |  | RLN3MA/MY26B016019, RIGHT |  | Below are the details for a new service call. o Site Name/#: Dollar General 22281 o Address: 5800 E 600 N, hamlet, IN, 46532. o Store Hours: 8am – 9pm (store will not stay past closing) o P2 – Medium (24-28 Hours) o PO: WO-0552080 o Problem: Check In/Out with Store Manager on Duty & Obtain Signature Hussmann R290 Microblock Equipment ONLY: serial # MY26B016019 - Lack of Refrigerant Asset Details: Productline Serial Number Module Assets Model Alt Name Microblock MY26B016019 center/right RLN3MA 3 Dr Freezer The store is currently operational and fully stocked with products. If this condition is not addressed immediately, it may result in product loss, food safety risk, and significant store operational impact, potentially leading to customer dissatisfaction. To prevent any product loss and ensure continued store operations, we request an P2 – Medium (24-28 Hours) level site visit. Checklist: • Verify the refrigerant charge level • If low, charge the system to the manufacturer-recommended level • Verify the TXV Setting • Inspect the evaporator coil for ice or frost accumulation • Verify the evaporator fan is active and running properly • Confirm airflow direction and un-obstructed air circulation • If ice is present: Perform a manual defrost to fully clear the evaporator coil • Verify Hot Gas Valve operation during defrosts • Confirm the condenser fan turns OFF during defrost • Tech can only work on multiple Hussmann R290 cases with one ticket, confirm all cases are operating or diagnose before leaving the store. • DO NOT work on existing cases, communicate to the Store MOD to place call with their service vendor. • Tech must list or take pictures of the data tag of all equipment model/serial number repaired on service ticket and provide a detail work summary of each equipment repaired. • If you need assistance, please contact the following Hussmann Technical Support Team @ 866-785-8499 or the following: 1) Todd Green @ 210-346-0005 2) Jeff Fosnaugh @ 314-501-8736 3) Andrew Miller @ 314-501-8698 • Hussmann Performance Parts @ 855-487-7778, option #3 – Warranty • Tecumseh compressor warranty – supply house will provide warranty tag to fill out & obtain a copy for office. Must purchase the compressor & file warranty claim. • If parts are not available & have long lead time, send an e-mail @ dg.service@hussmann.com to help locate. • Invoice MUST be submitted within 45 days of repair completion date to TAVANT. For support with warranty claim @ 800-398-7402, option #4 or hussmannwarrantyclaims@hussmann.com Send repair status with a brief work summary BEFORE leaving the location & contact to dg.service@hussmann.com. If you have any questions, contact us at @ dg.service@hussmann.com Troubleshooting Process Step 1 - Start with documentation located within case • Operation Manual & Data Sheet with the case. Step 2 - Scan Hussmann QR Code located on model/serial plate • Type serial number of case and follow navigation for product sheets, data sheets, and manuals Step 3 – Scan BOX QR Code for Box account • Carries in depth support - parameters, controller guides etc. Step 4 - Contact technical support - direct line #866-785-8499 • Tech support will escalate to our Field Equipment Team if issue cannot be resolved – tech support does not provide NTE/OT approval.
4d2e772d-3938-f111-88b5-000d3a1d8091 | FMT3KjvXNGHlSzz4h9AqmmKi+4/70QRevxyL3VkWGMKpqVsK0wDg71WlsKa5Z2mEd+zK1q4krypG+LnE14vITw== | 46135.7919 | 2026-04-14 12:36 |  | Posted | 2026-04-16 15:13 | WO-0552063 | Gulf | Dollar General #20876 | Elaine | AR | 4929321 | FEXA | WATER LEAK |  |  |  | RLN2MA/MY26B013812 | YES | Below are the details for a new service call. o Site Name/#: Dollar General 20876 o Address: 302 Main St Elaine, AR 72333 o Store Hours: 8am – 9pm (store will not stay past closing) o No Overtime o PO: WO-0552063 o Problem: Check In/Out with Store Manager on Duty & Obtain Signature Hussmann R290 Microblock Equipment ONLY: serial #MY26B013812 - Water is leaking under the unit. • Tech can only work on multiple Hussmann R290 cases with one ticket, confirm all cases are operating or diagnose before leaving the store. • DO NOT work on existing cases, communicate to the Store MOD to place call with their service vendor. • Tech must list or take pictures of the data tag of all equipment model/serial number repaired on service ticket and provide a detail work summary of each equipment repaired. • If you need assistance, please contact the following Hussmann Technical Support Team @ 866-785-8499 or the following: 1) Todd Green @ 210-346-0005 2) Jeff Fosnaugh @ 314-501-8736 3) Andrew Miller @ 314-501-8698 • Hussmann Performance Parts @ 855-487-7778, option #3 – Warranty • Tecumseh compressor warranty – supply house will provide warranty tag to fill out & obtain a copy for office. Must purchase the compressor & file warranty claim. • If parts are not available & have long lead time, send an e-mail @ dg.service@hussmann.com to help locate. • Invoice MUST be submitted within 45 days of repair completion date to TAVANT. For support with warranty claim @ 800-398-7402, option #4 or hussmannwarrantyclaims@hussmann.com Send repair status with a brief work summary BEFORE leaving the location & contact to dg.service@hussmann.com. If you have any questions, contact us at @ dg.service@hussmann.com Troubleshooting Process Step 1 - Start with documentation located within case • Operation Manual & Data Sheet with the case. Step 2 - Scan Hussmann QR Code located on model/serial plate • Type serial number of case and follow navigation for product sheets, data sheets, and manuals Step 3 – Scan BOX QR Code for Box account • Carries in depth support - parameters, controller guides etc. Step 4 - Contact technical support - direct line #866-785-8499 • Tech support will escalate to our Field Equipment Team if issue cannot be resolved – tech support does not provide NTE/OT approval. | 4/15/26 Seth Allen Arrived to check the back left case leaking water. I found the bottom of the doors sweating causing a very small amount of water on the floor. All freezer cases in the store sweat at the bottom as well but this is the only one where the water makes it to the floor. Checked temp and humidity in the area and found it was 79 degrees and 47% rh in the space between the stockroom door and this first case. Stockroom door is constantly be used and propped open to move stuff in and out. Stockroom only has one supply and return fed from sales floor unit with its space temp sensor also in the sales floor, causing the stockroom to not be able to maintain temp. Waiting on response from tech support for input. Resource: Seth Allen 4/16/26 Seth Allen Returned to recheck the water leak, talked with tech support and they stated if the area either exceeds the 55% humidity or 75 degree mark this will need to be addressed and is likely the cause of condensation at the bottom of the doors. Upon returning today i verified operation of the frame heaters and measured temp in the area. It was 75 degrees by this case and 76 in the stockroom. Almost no moisture on the floor in comparison to yesterday when it was in the 79 to 80 degree range. Temperature issues in this area will need to be fixed for the condensation to stop. Largely due to higher temps coming from the stockroom when the door is being used. Closing this call out as the contractor responsible for the hvac needs to investigate. Resource: Seth Allen
d1f1562e-3838-f111-88b5-000d3a9c8117 | IV2myHK2lM8++PEMfeDfrs6D7Vlfew50VO9cTev6Hh85XW+oHzKh1YlVoIJwUF37aM0AetDauePgq+q9eSc3Eg== | 46132.6255 | 2026-04-14 12:29 |  | Completed | 2026-04-14 17:43 | WO-0552056 | Phoenix, AZ | Dollar General #22286 | Arizona City | AZ | TAVANT/PRODUCT CARE | STORE CONNECT | ICE/FROST |  |  |  | RLN2MA/MY26B014938, LEFT |  | Job Scope: Coil Icing It has been observed that the coil icing issue in the refrigeration unit, which may impact cooling performance and system efficiency. Asset Details: Productline Serial Number Module Assets Model Alt Name Microblock MY26B014938 Left RLN2MA 2dr frzr The asset is currently operational and fully stocked with products. If this condition is not addressed immediately, it may result in product loss, food safety risk, and significant store operational impact, potentially leading to customer dissatisfaction. To prevent any product loss and ensure continued store operations, we request a Medium (24-28 Hours) level site visit. Checklist: • Verify the Defrost terminate Sensor is mounted at the Evap coil Outlet Pipe. • Check for any Coil Icing. • Verify the Operation of Hot gas Valve. o During defrost Hot Gas Valve must be open. • Verify the Operation of Condenser fan. o During Defrost Condenser Fan must be Off. • Verify the compressor Operation During Defrost. o Check whether the Compressor is tripping on Pressure Switch. • If Compressor is tripping on Pressure Switch, o Inspect the Switch functionality o Verify Valve operations. • Verify The Microblock Refrigerant Charge. o If Charge is low, adjust to the recommended level • Tech can only work on multiple Hussmann R290 cases with one ticket, confirm all cases are operating or diagnose before leaving the store. • DO NOT work on existing cases, communicate to the Store MOD to place call with their service vendor. • Tech must list or take pictures of the data tag of all equipment model/serial number repaired on service ticket and provide a detail work summary of each equipment repaired. • If you need assistance, please contact the following Hussmann Technical Support Team @ 866-785-8499 or the following: 1) Todd Green @ 210-346-0005 2) Jeff Fosnaugh @ 314-501-8736 3) Andrew Miller @ 314-501-8698 • Hussmann Performance Parts @ 855-487-7778, option #3 – Warranty • Tecumseh compressor warranty – supply house will provide warranty tag to fill out & obtain a copy for office. Must purchase the compressor & file warranty claim. • If parts are not available & have long lead time, send an e-mail @ dg.service@hussmann.com to help locate. • Invoice MUST be submitted within 45 days of repair completion date to TAVANT. For support with warranty claim @ 800-398-7402, option #4 or hussmannwarrantyclaims@hussmann.com Send repair status with a brief work summary BEFORE leaving the location & contact to dg.service@hussmann.com. If you have any questions, contact us at @ dg.service@hussmann.com Troubleshooting Process Step 1 - Start with documentation located within case • Operation Manual & Data Sheet with the case. Step 2 - Scan Hussmann QR Code located on model/serial plate • Type serial number of case and follow navigation for product sheets, data sheets, and manuals Step 3 – Scan BOX QR Code for Box account • Carries in depth support - parameters, controller guides etc. Step 4 - Contact technical support - direct line #866-785-8499 • Tech support will escalate to our Field Equipment Team if issue cannot be resolved – tech support does not provide NTE/OT approval. | Arrived at store checked in with manager and checked 2 door freezer. Freezer is running at -4.2. No signs of ice build up in case or on top from evap coil. Evap coil waa frosted up like normal. While here case went into defrost and coil cleared up. No issues found Resource: Ernesto Vega
2d4d4191-3638-f111-88b5-000d3a9c8117 | qMCUUizQP16sv2YRdMPJc6EYu+IM+grUHwzeJkRjY/RaYrJcsTO0K2qGs7Fs63YAVt32u+DFBJA2oczhx68ZmA== | 46132.6231 | 2026-04-14 12:17 |  | Completed | 2026-04-15 10:13 | WO-0552039 | Phoenix, AZ | Dollar General #14104 | Tucson | AZ | TAVANT/PRODUCT CARE | STORE CONNECT | TEMPERATURE/PARAMETER |  |  |  | RLN2MA/MY26B015990 Left |  | Response : Priority: P2 – Medium (24-28 Hours) Job Scope: Coil Icing It has been observed that the coil icing issue in the refrigeration unit, which may impact cooling performance and system efficiency. Asset Details: Productline Serial Number Module Assets Model Alt Name: Microblock MY26B015990 Left RLN2MA 2 Door Frozen Food The asset is currently operational and fully stocked with products. If this condition is not addressed immediately, it may result in product loss, food safety risk, and significant store operational impact, potentially leading to customer dissatisfaction. To prevent any product loss and ensure continued store operations, we request a Medium (24-28 Hours) level site visit. Tech must obtain a photo of the equipment tag that includes Model & Serial Number on the case and Condensing Unit (Tecumseh). Please review and Confirm the Checklist items below. Checklist: • Verify the Defrost terminate Sensor is mounted at the Evap coil Outlet Pipe. • Check for any Coil Icing, take pictures • Verify the Operation of Hot gas Valve. o During defrost Hot Gas Valve must be open. • Verify the Operation of Condenser fan. o During Defrost Condenser Fan must be Off. • Verify the compressor Operation During Defrost. o Check whether the Compressor is tripping on Pressure Switch. • If Compressor is tripping on Pressure Switch, o Inspect the Switch functionality o Verify Valve operations. • Verify The Microblock Refrigerant Charge. o If Charge is low, adjust to the recommended level | Arrived checked in went to case temping low. Current temp is at -17. Comp stays on and doesnt turn off. Went to condensor checked parameters on control. Suction is at 9psi and cut out is set for 5 psi and cut in at 15. Suctions stays at 9psi and doesnt pump down. Set parameter to 11psi and cut in at 22psi. Temp came down to -8 to -11psi. Will follow up tomorrow. Resource: Christopher Ruiz Returned temp was as low as -12. Adjusted differential to 3 degrees is was currently set to 7 degree swing now it goes from -6 to -9. Resource: Christopher Ruiz
029435b7-1c38-f111-88b5-000d3a9c8117 | oG2T9NdEo47c8fjpu+3CkL6EkVwUioV1dyLIJCLu1gWzcRyO/cmnF7mTBHlWGzjviNI+8A+4k2idZ2nZg6BMOw== | 46132.7559 | 2026-04-14 09:12 |  | Completed | 2026-04-21 06:00 | WO-0551833 | RPM/Strategic Accounts | Dollar General #21016 | San Angelo | TX | 4921327 | FEXA |  |  |  |  | RMN3MA/MY26B016499 |  | Site Name/#: Dollar General 21016 o Address: 950 GORDON BLVD SAN ANGELO, TX 76905 US o Store Hours: 8am – 9pm (store will not stay past closing) o No Overtime o PO: 4921327 o Problem: Check In/Out with Store Manager on Duty & Obtain Signature Hussmann R290 Microblock Equipment ONLY: Model#RMN3MA/Serial#MY26B016499 Identified that RIC03 is a newly installed unit. Noted installation is incomplete. Specifically, RIC03 lacks a drain pump, drain line, and drain collection pan.. Serial#MY26B016499 Please explain the issue Water is leaking under unit, Other (please list in comments section below) In case the service company or manufacturer needs to call the store, please confirm the store's phone number (include area code). 3259392305 · Tech can only work on multiple Hussmann R290 cases with one ticket, confirm all cases are operating or diagnose before leaving the store. · DO NOT work on existing cases, communicate to the Store MOD to place call with their service vendor. · Tech must list or take pictures of the data tag of all equipment model/serial number repaired on service ticket and provide a detail work summary of each equipment repaired. · If you need assistance, please contact the following Hussmann Technical Support Team @ 866-785-8499 or the following: 1) Todd Green @ 210-346-0005 2) Jeff Fosnaugh @ 314-501-8736 3) Andrew Miller @ 314-501-8698 · Hussmann Performance Parts @ 855-487-7778, option #3 – Warranty · Tecumseh compressor warranty – supply house will provide warranty tag to fill out & obtain a copy for office. Must purchase the compressor & file warranty claim. · If parts are not available & have long lead time, send an e-mail @ dg.service@hussmann.com to help locate. · Invoice MUST be submitted within 45 days of repair completion date to TAVANT. For support with warranty claim @ 800-398-7402, option #4 or hussmannwarrantyclaims@hussmann.com | Per Encore - call is complete Resource: ENCORE MECHANICAL LLC
deadc067-5d37-f111-88b5-7c1e5280004d | ioQyiYjYYtqddbt2eiB1itfk8cocQvMEyZKAJ7+PPezOjUwWsrzbxuFcYFv/g0WVxewV1Ad9Suo9CxLOcs8vug== | 46132.8761 | 2026-04-13 10:23 |  | Completed | 2026-04-13 18:08 | WO-0551078 | Houston, TX | Dollar General #14858 | Houston | TX | TAVANT/PRODUCT CARE | STORE CONNECT | NUISANCE, PRODUCT BLOCKING VENT |  |  |  | RLN2MA/MY26B016475, LEFT |  | EMER* Low refrigerant Operating condition on the MY26B016475, RLN2MA, LEFT refrigeration case at the above-mentioned location. The condition being found active for last 48 Hours. The store is currently operational and fully stocked with products. If this condition is not addressed immediately, it may result in product loss, food safety risk, and significant store operational impact, potentially leading to customer dissatisfaction. To prevent any product loss and ensure continued store operations, we request an immediate P1 (Critical) level site visit. Below are the details for a new service call. o Site Name/#: Dollar General 14858 o Address: 4750 W Fuqua ST Houston TX 77045 o Store Hours: 8am – 9pm (store will not stay past closing) o Overtime YES o PO: TAVANT/PRODUCT CARE o Problem: Check In/Out with Store Manager on Duty & Obtain Signature Hussmann R290 Microblock Equipment ONLY: We are observing Low refrigerant Operating condition on the MY26B016475, RLN2MA, LEFT refrigeration case at the above-mentioned location. The condition being found active for last 48 Hours. The store is currently operational and fully stocked with products. If this condition is not addressed immediately, it may result in product loss, food safety risk, and significant store operational impact, potentially leading to customer dissatisfaction. To prevent any product loss and ensure continued store operations, we request an immediate P1 (Critical) level site visit. Checklist: • Verify the refrigerant charge level • If low, charge the system to the manufacturer-recommended level • Inspect the evaporator coil for ice or frost accumulation • Verify the evaporator fan is active and running properly • Confirm airflow direction and un-obstructed air circulation • If ice is present: Perform a manual defrost to fully clear the evaporator coil • Verify Hot Gas Valve operation during defrosts • Confirm the condenser fan turns OFF during defrost • Tech must contact Store Connect via Microsoft Teams to Vin – Vinodrajan Paramasivam before leaving the store to confirm reading/repair is fix. Tech MUST contact Hussmann Connect Solutions via TEAMS when on site & before leaving the store: <insert names> • Tech can only work on multiple Hussmann R290 cases with one ticket, confirm all cases are operating or diagnose before leaving the store. • DO NOT work on existing cases, communicate to the Store MOD to place call with their service vendor. • Tech must list or take pictures of the data tag of all equipment model/serial number repaired on service ticket and provide a detail work summary of each equipment repaired. • If you need assistance, please contact the following Hussmann Technical Support Team @ 866-785-8499 or the following: 1) Todd Green @ 210-346-0005 2) Jeff Fosnaugh @ 314-501-8736 3) Andrew Miller @ 314-501-8698 • Hussmann Performance Parts @ 855-487-7778, option #3 – Warranty • Tecumseh compressor warranty – supply house will provide warranty tag to fill out & obtain a copy for office. Must purchase the compressor & file warranty claim. • If parts are not available & have long lead time, send an e-mail @ dg.service@hussmann.com to help locate. • Invoice MUST be submitted within 45 days of repair completion date to TAVANT. For support with warranty claim @ 800-398-7402, option #4 or hussmannwarrantyclaims@hussmann.com Send repair status with a brief work summary BEFORE leaving the location & contact to dg.service@hussmann.com. If you have any questions, contact us at @ dg.service@hussmann.com Troubleshooting Process Step 1 - Start with documentation located within case • Operation Manual & Data Sheet with the case. Step 2 - Scan Hussmann QR Code located on model/serial plate • Type serial number of case and follow navigation for product sheets, data sheets, and manuals Step 3 – Scan BOX QR Code for Box account • Carries in depth support - parameters, controller guides etc. Step 4 - Contact technical support - direct line #866-785-8499 • Tech support will escalate to our Field Equipment Team if issue cannot be resolved – tech support does not provide NTE/OT approval. | *Call from Store Connect, branch submit to Tavant*Located reach-in freezer alarming high temp. No airflow on 2 door case. Found product covering return. Set through a manual defrost and cleared up product from return. Monitored case come out of defrost and drop down in temp. Good airflow back at case. All checks out ok. Resource: Ruben Guzman
d639e045-1e35-f111-88b4-000d3a1d89f0 | r8wQwVAY60eZEFywyuUFFEeSkSTc67LMVviGLe3rakvY87BSGUqQM507MStSTYFwZ+uNiAQvQ68l3u1AoY+NtQ== | 46125.9558 | 2026-04-10 13:46 |  | Completed | 2026-04-11 06:00 | WO-0549951 | RPM/Strategic Accounts | Dollar General #21223 | Santa Anna | TX | TAVANT/TIM SMITH | TIM SMITH | REFRIGERANT, NO CHARGE | [5 empty] | Below are the details for a new service call. o Site Name/#: Dollar General 21223 o Address: o Store Hours: 8am – 9pm (store will not stay past closing) o No Overtime o PO: TAVANT/TIM SMITH o Problem: Check In/Out with Store Manager on Duty & Obtain Signature Hussmann R290 Microblock Equipment ONLY: Check Refrigeration Equipment • Tech can only work on multiple Hussmann R290 cases with one ticket, confirm all cases are operating or diagnose before leaving the store. • DO NOT work on existing cases, communicate to the Store MOD to place call with their service vendor. • Tech must list or take pictures of the data tag of all equipment model/serial number repaired on service ticket and provide a detail work summary of each equipment repaired. • If you need assistance, please contact the following Hussmann Technical Support Team @ 866-785-8499 or the following: 1) Todd Green @ 210-346-0005 2) Jeff Fosnaugh @ 314-501-8736 3) Andrew Miller @ 314-501-8698 • Hussmann Performance Parts @ 855-487-7778, option #3 – Warranty • Tecumseh compressor warranty – supply house will provide warranty tag to fill out & obtain a copy for office. Must purchase the compressor & file warranty claim. • If parts are not available & have long lead time, send an e-mail @ dg.service@hussmann.com to help locate. • Invoice MUST be submitted within 45 days of repair completion date to TAVANT. For support with warranty claim @ 800-398-7402, option #4 or hussmannwarrantyclaims@hussmann.com | Encore was on site Saturday. Resource: ENCORE MECHANICAL LLC
99328c62-4934-f111-88b4-7c1e5257ceaa | Vdnaxj44fPU5G0/TYit3We/EX7o3djWLmCovxbCOeLsxYei6jqP430vQhuubvZ8kQlFVzKboB6Ndm2qF+8SBzg== | 46126.664 | 2026-04-09 12:22 |  | Completed | 2026-04-09 13:00 | WO-0549298 | RPM/Strategic Accounts | Dollar General #21016 | San Angelo | TX | 4918766 | FEXA |  |  |  |  | RLN2MA/MY26B015995 |  | o Site Name/#: Dollar General 21016 o Address: 950 GORDON BLVD SAN ANGELO, TX 76905 US o Store Hours: 8am – 9pm (store will not stay past closing) o No Overtime o PO: 4918766 o Problem: Check In/Out with Store Manager on Duty & Obtain Signature Hussmann R290 Microblock Equipment ONLY: RLN2MA, MY26B015995 Not working at all need fixed asap had a remodel and our fresh truck is on its way 700 piece truck and that freezer is out not working at all fix asap · Tech can only work on multiple Hussmann R290 cases with one ticket, confirm all cases are operating or diagnose before leaving the store. · DO NOT work on existing cases, communicate to the Store MOD to place call with their service vendor. · Tech must list or take pictures of the data tag of all equipment model/serial number repaired on service ticket and provide a detail work summary of each equipment repaired. · If you need assistance, please contact the following Hussmann Technical Support Team @ 866-785-8499 or the following: 1) Todd Green @ 210-346-0005 2) Jeff Fosnaugh @ 314-501-8736 3) Andrew Miller @ 314-501-8698 · Hussmann Performance Parts @ 855-487-7778, option #3 – Warranty · Tecumseh compressor warranty – supply house will provide warranty tag to fill out & obtain a copy for office. Must purchase the compressor & file warranty claim. · If parts are not available & have long lead time, send an e-mail @ dg.service@hussmann.com to help locate. · Invoice MUST be submitted within 45 days of repair completion date to TAVANT. For support with warranty claim @ 800-398-7402, option #4 or hussmannwarrantyclaims@hussmann.com | Call completed Resource: ENCORE MECHANICAL LLC
5a61427c-4634-f111-88b4-7c1e5257ceaa | XZSvsysYC7jytiYjbtxmOdVX9SKnu/RbA74aIy/i0LyF3Lknb56RaRf8NB6HfzGnJ7P5n3WK9cT+8rXtedMVPw== | 46124.9776 | 2026-04-09 12:01 |  | Completed | 2026-04-10 08:30 | WO-0549280 | RPM/Strategic Accounts | Dollar General #20407 | Abilene | TX | TAVANT/PRODUCT CARE | STORE CONNECT | NUISANCE |  |  |  | RLN3MA/MY26B016017, RIGHT |  | Dispatch Reason: High Temperature Alarm We are observing a High Temperature Alarm on the Serial number MY26B016017, Model: RLN3MA, Center/right microblock case at the above-mentioned location. The alarm has been active beyond the configured threshold of 60 minutes. BILL this call to TaVANt The store is currently operational. If this condition is not addressed immediately, it may result in product loss, food safety risk, and significant store operational impact, potentially leading to customer dissatisfaction. To prevent any product loss and ensure continued store operations, we request an immediate P1 (Critical) level site visit. Checklist: • Inspect the evaporator coil for ice or frost accumulation • Verify the evaporator fan is active and running properly • Confirm airflow direction and un-obstructed air circulation • If ice is present: Perform a manual defrost to fully clear the evaporator coil • Verify Hot Gas Valve operation during defrosts • Confirm the condenser fan turns OFF during defrost • Verify the refrigerant charge level o If low, charge the system to the manufacturer-recommended level | Per Jay B - Tech onsite 4/10 fixed Resource: ENCORE MECHANICAL LLC
54872070-9833-f111-88b4-7c1e5257c77a | zukOUUnvLKLXu/wdAcZm9rV5ePcUJt3rAccXSjo1YWXN27nZeF7P6QEytOidH/0S6pQWKMmCilp9tkQKVWQW9g== | 46141.0927 | 2026-04-08 15:16 |  | Posted | 2026-04-17 11:41 | WO-0548822 | Gulf | Dollar General #13338 | McRae | AR | TAVANT/TIM SMITH | TIM SMITH | CAREL CONTROLLER, REPLACEMENT | CAREL CONTROLLERS & CABLING |  |  | RLN2MA/MY26B013807, RLN3MA/MY26B013833, RMN5MA/MY26B013852 |  | o Store Hours: 8am – 9pm (store will not stay past closing) o OT Approved o PO: Tavant/Product Care o Problem: Check In/Out with Store Manager on Duty & Obtain Signature Hussmann R290 Microblock Equipment ONLY: Replacement of Controllers on 4 Cases: MY21G066701 (RFMN4)---dixel(does not require Tecumseh) ~MY26B013852 (RMN5MA)---Carel controllers, 2 med controllers Carel~MY26B013833 (RLN3MA)-- Carel controllers, 2 low controllers Carel~MY26B013807 (RLN2MA)--- Carel controller,1 low controllers Carel. Tech must contact Store Connect via Microsoft Teams to “Vin” = Vinodrajan Paramasivam. Tech must obtain a photo of the equipment tag that includes Model & Serial Number on the case and Condensing Unit (Tecumseh). Please review and Confirm the Checklist items below. • Tech can only work on multiple Hussmann R290 cases with one ticket, confirm all cases are operating or diagnose before leaving the store. • DO NOT work on existing cases, communicate to the Store MOD to place call with their service vendor. • Tech must list or take pictures of the data tag of all equipment model/serial number repaired on service ticket and provide a detail work summary of each equipment repaired. • If you need assistance, please contact the following Hussmann Technical Support Team @ 866-785-8499 or the following: 1) Todd Green @ 210-346-0005 2) Jeff Fosnaugh @ 314-501-8736 3) Andrew Miller @ 314-501-8698 • Hussmann Performance Parts @ 855-487-7778, option #3 – Warranty • Tecumseh compressor warranty – supply house will provide warranty tag to fill out & obtain a copy for office. Must purchase the compressor & file warranty claim. • If parts are not available & have long lead time, send an e-mail @ dg.service@hussmann.com to help locate. • Invoice MUST be submitted within 45 days of repair completion date to TAVANT. For support with warranty claim @ 800-398-7402, option #4 or hussmannwarrantyclaims@hussmann.com Send repair status with a brief work summary BEFORE leaving the location & contact to dg.service@hussmann.com. If you have any questions, contact us at @ dg.service@hussmann.com | 4/8/26Tech: kris clark Arrived onsite and checked in. I walked the site and did not find the serial associated with the second part of my job scope, i signed into store connect and search the asset to find the asset with an address in arizona. I need to reach out to the care team as it appears 2 calls were accidentally merged into one. Parts are on order for the first part of the job scope and i will return when parts arrive. Resource: Kristopher Clark 4/15/26 Tech: Kris Clark beverage case HUSSMANN MODEL: RMN4MA SERIAL: MY26B013849 BEVERAGE LEFT TECUMSEH MODEL:TCX413U-DS1B01 SERIAL:04C0326120755 BEVERAGE RIGHT TECUMSEH MODEL: TCX413U-DS1B01 SERIAL:04C0226120754 FROZEN FOOD 4 CASE HUSSMANN MODEL:RLN2MA SERIAL:MY26B013807 FROZEN FOOD CONDENSER TECUMSEH MODEL:ALX440UDS3B01 SERIAL:04C0426120787 FROZEN FOOD 5 CASE HUSSMANN MODEL:RLN3MA SERIAL:MY26B013833 FROZEN FOOD 5 LEFT TECUMSEH MODEL:ALX440U-DS3B01 SERIAL:04C0426120785 FROZEN FOOD 5 RIGHT TECUMSEH MODEL:ALX440U-DS3B01 SERIAL:04C0426120780 DELI MEAT HUSSMANN MODEL:RFMN4 SERIAL:MY21G066701 FRESH FOOD CASE HUSSMANN MODEL:RMN5MA SERIAL:MY26B013852 FRESH FOOD LEFT TECUMSEH MODEL:TCX413U-DS1B01 SERIAL: 04C0226120736 FRESH FOOD RIGHT TECUMSEH MODEL: TCX413U-DS1BO1 SERIAL: 04C0326120770 Arrived onsite and check in. I replaced the controllers on the effeccted cases,set the network addresses, removed and ran a new comm. loop for the store. the site is now online in store connect. job is complete. Resource: Kristopher Clark
45db8177-6733-f111-88b3-6045bdebb2f7 | d/pHlKjkOUeFyWRTL1fvf8g/wl+kTDpPfFz3sIwVlwE+je58d15CvlOc9b2/yckW3b3OaZn1DHHMEp8wsA+4Ww== | 46124.9732 | 2026-04-08 09:25 |  | Completed | 2026-04-08 11:00 | WO-0548436 | RPM/Strategic Accounts | Dollar General #3270 | San Angelo | TX | TAVANT/RPM - 4915951 | FEXA | CASSETTE, REPLACEMENTE | CASSETTE - 2qty |  |  | MY26B016515 |  | o Site Name/#: Dollar General 3270 o Address: 2934 N CHADBOURNE ST SAN ANGELO, TX 76903 US o Store Hours: 8am – 9pm (store will not stay past closing) o No Overtime o PO: 4915951 o Problem: Check In/Out with Store Manager on Duty & Obtain Signature Hussmann R290 Microblock Equipment ONLY: MY26B016515, Not working at all • Tech can only work on multiple Hussmann R290 cases with one ticket, confirm all cases are operating or diagnose before leaving the store. • DO NOT work on existing cases, communicate to the Store MOD to place call with their service vendor. • Tech must list or take pictures of the data tag of all equipment model/serial number repaired on service ticket and provide a detail work summary of each equipment repaired. • If you need assistance, please contact the following Hussmann Technical Support Team @ 866-785-8499 or the following: 1) Todd Green @ 210-346-0005 2) Jeff Fosnaugh @ 314-501-8736 3) Andrew Miller @ 314-501-8698 • Hussmann Performance Parts @ 855-487-7778, option #3 – Warranty • Tecumseh compressor warranty – supply house will provide warranty tag to fill out & obtain a copy for office. Must purchase the compressor & file warranty claim. • If parts are not available & have long lead time, send an e-mail @ dg.service@hussmann.com to help locate. • Invoice MUST be submitted within 45 days of repair completion date to TAVANT. For support with warranty claim @ 800-398-7402, option #4 or hussmannwarrantyclaims@hussmann.com Send repair status with a brief work summary BEFORE leaving the location & contact to dg.service@hussmann.com. If you have any questions, contact us at @ dg.service@hussmann.com Troubleshooting Process Step 1 - Start with documentation located within case • Operation Manual & Data Sheet with the case. Step 2 - Scan Hussmann QR Code located on model/serial plate • Type serial number of case and follow navigation for product sheets, data sheets, and manuals Step 3 – Scan BOX QR Code for Box account • Carries in depth support - parameters, controller guides etc. Step 4 - Contact technical support - direct line #866-785-8499 • Tech support will escalate to our Field Equipment Team if issue cannot be resolved – tech support does not provide NTE/OT approval. | Jay confirmed - call completed Resource: ENCORE MECHANICAL LLC
fef3814b-ca32-f111-88b3-6045bddbb098 | AFd5bVF0BVhWOLVNOQ/lteu0SjGIaSsYVe4NqnOuMWtO2sF9Qc0upJpmPhbYEQYHXcFnO8fn9YUV9Uepy3ArmA== | 46126.6928 | 2026-04-07 14:40 |  | Completed | 2026-04-10 16:18 | WO-0548123 | Houston, TX | Dollar General #14858 | Houston | TX | TAVANT/PRODUCT CARE | STORE CONNECT | EVAPORATOR FAILURE |  |  |  | RMN5MA/MY26B016546, LEFT |  | Tech must contact Store Connect via Microsoft Teams to Vin – Vinodrajan Paramasivam before leaving the store to confirm reading/repair is fix. 2 BUS DAYS* Evaporator Fan Failure or Disconnected Tech must obtain a photo of the equipment tag that includes Model & Serial Number on the case and Condensing Unit (Tecumseh). Please review and Confirm the Checklist items below. We are observing an Evaporator Fan Failure or Disconnected condition on the Serial number MY26B016546, Model: RMN5MA, LEFT micro block case at the above-mentioned location. The condition being found active for more than last 24 hours. The store is currently operational. If this condition is not addressed immediately, it may result in product loss, food safety risk, and significant store operational impact, potentially leading to customer dissatisfaction. To prevent any product loss and ensure continued store operations, we request an P2-Medium (24-48 Hours) level site visit. o Site Name/#: Dollar General 14858 o Address: 4750 W Fuqua St , HOUSTON , TX , US - 77045 o Store Hours: 8am – 9pm (store will not stay past closing) o No Overtime o PO: TAVANT/Product Care o Problem: Check In/Out with Store Manager on Duty & Obtain Signature Hussmann R290 Microblock Equipment ONLY: P2 – Medium (24-28 Hours) Job Scope: Evaporator Fan Failure or Disconnected Tech must obtain a photo of the equipment tag that includes Model & Serial Number on the case and Condensing Unit (Tecumseh). Please review and Confirm the Checklist items below. We are observing an Evaporator Fan Failure or Disconnected condition on the Serial number MY26B016546, Model: RMN5MA, LEFT micro block case at the above-mentioned location. The condition being found active for more than last 24 hours. The store is currently operational. If this condition is not addressed immediately, it may result in product loss, food safety risk, and significant store operational impact, potentially leading to customer dissatisfaction. To prevent any product loss and ensure continued store operations, we request an P2-Medium (24-48 Hours) level site visit. Checklist: • Verify the evaporator fan is active and running properly. • Confirm airflow direction and un-obstructed air circulation • If Evaporator Fan Found not active, Verify the Electrical Connection.(The Evaporator Fan should be Connected in NO3). • If any loose contact found, secure the Connection Properly. • Once Connection Secured, Verify the Fan operation again. • Inspect the evaporator coil for ice or frost accumulation • If ice is present: Perform a manual defrost to fully clear the evaporator coil • Confirm the condenser fan turns OFF during defrost. Tech MUST contact Hussmann Connect Solutions via TEAMS when on site & before leaving the store: <insert names> • Tech can only work on multiple Hussmann R290 cases with one ticket, confirm all cases are operating or diagnose before leaving the store. • DO NOT work on existing cases, communicate to the Store MOD to place call with their service vendor. • Tech must list or take pictures of the data tag of all equipment model/serial number repaired on service ticket and provide a detail work summary of each equipment repaired. • If you need assistance, please contact the following Hussmann Technical Support Team @ 866-785-8499 or the following: 1) Todd Green @ 210-346-0005 2) Jeff Fosnaugh @ 314-501-8736 3) Andrew Miller @ 314-501-8698 • Hussmann Performance Parts @ 855-487-7778, option #3 – Warranty • Tecumseh compressor warranty – supply house will provide warranty tag to fill out & obtain a copy for office. Must purchase the compressor & file warranty claim. • If parts are not available & have long lead time, send an e-mail @ dg.service@hussmann.com to help locate. • Invoice MUST be submitted within 45 days of repair completion date to TAVANT. For support with warranty claim @ 800-398-7402, option #4 or hussmannwarrantyclaims@hussmann.com Send repair status with a brief work summary BEFORE leaving the location & contact to dg.service@hussmann.com. If you have any questions, contact us at @ dg.service@hussmann.com | 4/8/26 RCortez - Arrived on site. Checked in with manager. Checked reach-in case and found door open. Found 4 out of five doors not closing automatically. Adjusted tension on torque rods. Found one evaporator fan motor not running dor left side of case. Right side is refrigerating normally. Could not access evaporator from top of unit. Will return to continue teoubleshooting. Left the left side of case deenergized to avoid compressor damage. Spoke with Tamara Jimmeson before leaving. Resource: Raymond Cortez 4/10/26 RCortez - Arrived on site. Checked in with manager. Removed product from shelving to gain access to evaporator fans and verify running/not running. Checked wiring above case. Found wires on Carel controller terminals extremely loose and wires disconnected from output "NO3" and "C1". Connected wiring and tightened connections. Secured wiring and restored power to skid. Verified evaporator fans running. Placed back shelving and product. Monitored case temp. Case pulled down to 36DF. No other issues found. Contacted Hussmann Tech support to complete WO. Spoke with Alvaro Perez before leaving. WO completed. Resource: Raymond Cortez
3e79be73-f431-f111-88b4-7c1e5257c08f | CRRZcykM6qcHaysrlKHTF188peoYB1BSUmVmOjUhlXF6+ARjpAIdKwz9Kwr81Dfsmgd0AxddA4sfHJwgI2VQwg== | 46133.8035 | 2026-04-06 13:09 |  | Completed | 2026-04-14 06:01 | WO-0547346 | Gulf | Dollar General #6827 | Conway | AR | 4910585 | FEXA | TEMPERATURE |  |  |  | RLN2MA/MY26b013811 ~ RLN3MA/MY26B013832 |  | Below are the details for a new service call. o Site Name/#: Dollar General 6827 o Address: 1600 E Oak St Conway Arkansas 72032 o Store Hours: 8am – 9pm (store will not stay past closing) o yes Overtime Approved o PO: 4910585 o Problem: Check In/Out with Store Manager on Duty & Obtain Signature Hussmann R290 Microblock Equipment ONLY: rl2ma – my26b013811 these freezers are not keeping temp.!!! - rln3ma- my26b013832 - temp just read 82 degrees now saying defrosting... but not resetting!!! Tech can only work on multiple Hussmann R290 cases with one ticket, confirm all cases are operating or diagnose before leaving the store. DO NOT work on existing cases, communicate to the Store MOD to place call with their service vendor. Tech must list or take pictures of the data tag of all equipment model/serial number repaired on service ticket and provide a detail work summary of each equipment repaired. If you need assistance, please contact the following Hussmann Technical Support Team @ 866-785-8499 or the following: Todd Green @ 210-346-0005 Jeff Fosnaugh @ 314-501-8736 Andrew Miller @ 314-501-8698 Hussmann Performance Parts @ 855-487-7778, option #3 – Warranty Tecumseh compressor warranty – supply house will provide warranty tag to fill out & obtain a copy for office. Must purchase the compressor & file warranty claim. If parts are not available & have long lead time, send an e-mail @ dg.service@hussmann.com to help locate. Invoice MUST be submitted within 45 days of repair completion date to TAVANT. For support with warranty claim @ 800-398-7402, option #4 or hussmannwarrantyclaims@hussmann.com Send repair status with a brief work summary BEFORE leaving the location & contact to dg.service@hussmann.com. If you have any questions, contact us at @ dg.service@hussmann.com Troubleshooting Process Step 1 - Start with documentation located within case Operation Manual & Data Sheet with the case. Step 2 - Scan Hussmann QR Code located on model/serial plate Type serial number of case and follow navigation for product sheets, data sheets, and manuals Step 3 – Scan BOX QR Code for Box account Carries in depth support - parameters, controller guides etc. Step 4 - Contact technical support - direct line #866-785-8499 Tech support will escalate to our Field Equipment Team if issue cannot be resolved – tech support does not provide NTE/OT approval. | 4/7/26 Tech: kris clark Frozen food 4 Condenser : Model: ALX440U - DS3B01 Serial: 04B2826120722 Case: Model:RLN2MA Serial: MY26B013811 Frozen food 5 Left condenser: Model:ALX440U- DS3B01 Serial:04B2826120723 Right condenser: Model:ALX44OU -DS3B01 Serial: 04B2826120718 Case: Model:RLN3MA serial:MY26B013832 Arrived onsite and spoke with the manager. She stated that both frozen food 4 and 5 were going in and out of defrost and showing high temp and then randomly started working. I pulled the log in all 3 controllers and found that all 3 rose in temperature around 1030am on 4/6 with a call for cooling. They started to recover, went through a defrost and stayed in a high temperature state before pulling down. I have pulled as many graphs as i could and i will need to review it with technical support. I do see one of the coil temp sensor for frozen food 5 is at a higher temperature than expected. I will need to investigate that. I forced a defrost and noticed i have a 10+/-2 degree difference in my compressor discharge temperatures while in defrost. The system recovered fairly quick once it started cooling after defrost. I will speak with technical support and return. Resource: Kristopher Clark 4/8/26 Tech: Kris Clark space temp:72 humidity:41% Returned to the site and took frozen food microblocks covers off to check for ice, i found some ice buildup on the right unit but no ice on the coil. it was on the suction line around the sensing bulb and in the corner of the drain pan, i cleared the ice, checked the coil sensor with ice water and confirmed that it is reading correctly. i synced the times for the case and started a manual defrost to sync the defrosts together. I spoke with engineering about the compressor discharge temps showing a difference of 10+ degrees and it is normal for this setup. The box is cycling at temp. at this time and i do not see any issues. I will leave the ticket open for a day to monitor and return if needed. Resource: Kristopher Clark reviewed the systems remotely and they are holding temp. job is complete Resource: Kristopher Clark
598336bd-8e30-f111-88b4-000d3a1d8efd | cNjEUbwAZ/U34ulNB2rJpNGTQXBqpJvPTlJDlnzAguLU4A+N9XLBXPhzv6aM3eEIViuQnO64WFrS+OGuXkiTLg== | 46126.5871 | 2026-04-04 18:29 |  | Posted | 2026-04-07 11:53 | WO-0546538 | Gulf | Dollar General #20876 | Elaine | AR | 4906543 | FEXA | WATER LEAK |  |  |  | RLN2MA/MY26B013812 |  | Below are the details for a new service call. o Site Name/#: Dollar General 20876 o Address: 302 MAIN ST, ELAINE, AR 72333 o Store Hours: 8am – 9pm (store will not stay past closing) o No Overtime o PO: 4906543 o Problem: Check In/Out with Store Manager on Duty & Obtain Signature Hussmann R290 Microblock Equipment ONLY: RLN2MA / MY26B013812 Water is leaking under unit • Tech can only work on multiple Hussmann R290 cases with one ticket, confirm all cases are operating or diagnose before leaving the store. • DO NOT work on existing cases, communicate to the Store MOD to place call with their service vendor. • Tech must list or take pictures of the data tag of all equipment model/serial number repaired on service ticket and provide a detail work summary of each equipment repaired. • If you need assistance, please contact the following Hussmann Technical Support Team @ 866-785-8499 or the following: 1) Todd Green @ 210-346-0005 2) Jeff Fosnaugh @ 314-501-8736 3) Andrew Miller @ 314-501-8698 • Hussmann Performance Parts @ 855-487-7778, option #3 – Warranty • Tecumseh compressor warranty – supply house will provide warranty tag to fill out & obtain a copy for office. Must purchase the compressor & file warranty claim. • If parts are not available & have long lead time, send an e-mail @ dg.service@hussmann.com to help locate. • Invoice MUST be submitted within 45 days of repair completion date to TAVANT. For support with warranty claim @ 800-398-7402, option #4 or hussmannwarrantyclaims@hussmann.com Send repair status with a brief work summary BEFORE leaving the location & contact to dg.service@hussmann.com. If you have any questions, contact us at @ dg.service@hussmann.com | 47/26 Tech: kris clark Case: Model: RLN2MA Serial: MY26B013812 Condenser skid: Serial: 04C0426120788 Model: ALX440U-DS3B01 Arrived onsite and checked in. I found no water around any of the cases, i spoke with the store manager and she stated it was multiple cases new and old across the store. The store is currently 71 degrees at 35% humidity. The site's service provider was onsite and mentioned the hvac was down but it was repaired recently and the site struggles with humidity. I put the system in defrost and checked all functions and everything is working as it should. Job is complete. Resource: Kristopher Clark
1dc8eaa6-e12e-f111-88b4-6045bddb9d4c | CVjRwWVmC3cNvQq/YVdTOo53SjNjQp7vuNxoqxRJskZwcV4b18ZNwpzNAPKDelr8sCLYWheLVFj8MixnubxmMQ== | 46135.0277 | 2026-04-02 15:17 |  | Completed | 2026-04-03 09:32 | WO-0545463 | Phoenix, AZ | DOLLAR GENERAL #10369 | Ajo | AZ | TAVANT/PRODUCT CARE HUS-1118021 | STORE CONNECT | WIRING/CONTROLLER |  |  |  | RMN4MA/MY26B016036, LEFT |  | Store Hours: 8am – 9pm (store will not stay past closing) o OT Approved o PO: Tavant/Product Care o Problem: Check In/Out with Store Manager on Duty & Obtain Signature Hussmann R290 Microblock Equipment ONLY: Job Scope: Lack of Refrigerant Tech must obtain a photo of the equipment tag that includes Model & Serial Number on the case and Condensing Unit (Tecumseh). Please review and Confirm the Checklist items below. We are observing Low refrigerant Operating condition on the MY26B016036, RMN4MA, LEFT refrigeration case at the above-mentioned location. The condition being found active for last 48 Hours. The store is currently operational and fully stocked with products. If this condition is not addressed immediately, it may result in product loss, food safety risk, and significant store operational impact, potentially leading to customer dissatisfaction. To prevent any product loss and ensure continued store operations, we request an immediate P1 (Critical) level site visit. Checklist: • Verify the refrigerant charge level • If low, charge the system to the manufacturer-recommended level • Inspect the evaporator coil for ice or frost accumulation • Verify the evaporator fan is active and running properly • Confirm airflow direction and un-obstructed air circulation • If ice is present: Perform a manual defrost to fully clear the evaporator coil • Verify Hot Gas Valve operation during defrosts • Confirm the condenser fan turns OFF during defrost Tech can only work on multiple Hussmann R290 cases with one ticket, confirm all cases are operating or diagnose before leaving the store. DO NOT work on existing cases, communicate to the Store MOD to place call with their service vendor. Tech must list or take pictures of the data tag of all equipment model/serial number repaired on service ticket and provide a detail work summary of each equipment repaired. If you need assistance, please contact the following Hussmann Technical Support Team @ 866-785-8499 or the following: Todd Green @ 210-346-0005 Jeff Fosnaugh @ 314-501-8736 Andrew Miller @ 314-501-8698 Hussmann Performance Parts @ 855-487-7778, option #3 – Warranty Tecumseh compressor warranty – supply house will provide warranty tag to fill out & obtain a copy for office. Must purchase the compressor & file warranty claim. If parts are not available & have long lead time, send an e-mail @ dg.service@hussmann.com to help locate. Invoice MUST be submitted within 45 days of repair completion date to TAVANT. For support with warranty claim @ 800-398-7402, option #4 or hussmannwarrantyclaims@hussmann.com | Made contact with the management, found the case was holding temp at 37⁰, found that one side ( left circuit ) of the case was not moving airflow, found the evaporator coil was iced up, found the evaporator fan wasn't running, found the power wire was not connected to the Carel controller. I connected the wire to the controller, checked amp draws ( 0.4 amps ), ran the circuit through four defrost cycles till the ice was fully melted, and allowed the case to drop temperature. The case is a time off defrost, confirmed the condensing unit fully shuts down and the fan stays running. Confirmed the airflow direction. The case is now holding at 36⁰ on both circuits and is operating as it should at this time. Resource: Erich McGhee Closing the tocket Resource: Erich McGhee
c5b7f627-dd2e-f111-88b4-6045bddb9d4c | L71wnIZ+H7uas6v5dQTAxjYgSlKhyj3Sr+QLH++xFb4rJlvoCSxjQLy66N0LR+7tavg6Tzso4m+YNOliq5NcAA== | 46126.6925 | 2026-04-02 14:45 |  | Completed | 2026-04-03 11:01 | WO-0545426 | Houston, TX | Dollar General #12879 | Dickinson | TX | TAVANT/PRODUCT CARE | STORE CONNECT | SENSOR |  |  |  | RMN5MA/MY26B016549, LEFT |  | o Store Hours: 8am – 9pm (store will not stay past closing) o Overtime Approved o PO: Tavant/Product Care o Problem: Check In/Out with Store Manager on Duty & Obtain Signature Hussmann R290 Microblock Equipment ONLY: Sensor Swap - Defrost Terminate and Discharge Air Tech must obtain a photo of the equipment tag that includes Model & Serial Number on the case and Condensing Unit (Tecumseh). Please review and Confirm the Checklist items below. Dispatch Reason: Sensor Swap - Defrost Terminate We are observing a Sensor Swap condition on the Serial number MY26B016549, Model: RMN5MA, LEFT Module between the Defrost Terminate Sensor and the Control Temperature Sensor on the Micro block refrigeration case at the above-mentioned location. The alarm has remained active beyond the configured threshold 60 minutes. The store is currently operational and fully stocked with products. If this condition is not corrected in a timely manner, it may result in incorrect temperature control, improper defrost operation, energy wastage, potential product loss, and overall store operational impact, which could negatively affect case performance and product integrity. To prevent escalation and potential equipment or product impact, we request a P2 (High) priority site visit. Checklist: • Confirm that the Defrost Terminate Sensor is connected to the correct controller input terminal between S2 and Gnd. • Confirm that the Discharge Air Sensor is connected to its designated controller terminal between S1 and Gnd. • Verify that the Defrost Terminate probe is properly mounted at the evaporator coil termination/outlet point. • Verify the Discharge Air probe is mounted in the supply (discharge) air outlet path • Check for Discharge Air Sensor by: • Holding probe by hand and observing temperature response on the controller display • If a sensor swap is identified: o Correct the sensor wiring and probe positions o Verify normal defrost operation, accurate temperature readings, o Verify all the alarm clear (if any Present). Tech MUST contact Hussmann Connect Solutions via TEAMS when on site & before leaving the store: <insert names> Tech can only work on multiple Hussmann R290 cases with one ticket, confirm all cases are operating or diagnose before leaving the store. DO NOT work on existing cases, communicate to the Store MOD to place call with their service vendor. Tech must list or take pictures of the data tag of all equipment model/serial number repaired on service ticket and provide a detail work summary of each equipment repaired. If you need assistance, please contact the following Hussmann Technical Support Team @ 866-785-8499 or the following: Todd Green @ 210-346-0005 Jeff Fosnaugh @ 314-501-8736 Andrew Miller @ 314-501-8698 Hussmann Performance Parts @ 855-487-7778, option #3 – Warranty Tecumseh compressor warranty – supply house will provide warranty tag to fill out & obtain a copy for office. Must purchase the compressor & file warranty claim. If parts are not available & have long lead time, send an e-mail @ dg.service@hussmann.com to help locate. Invoice MUST be submitted within 45 days of repair completion date to TAVANT. For support with warranty claim @ 800-398-7402, option #4 or hussmannwarrantyclaims@hussmann.com Send repair status with a brief work summary BEFORE leaving the location & contact to dg.service@hussmann.com. If you have any questions, contact us at @ dg.service@hussmann.com | 04-03-26 juan olvera tech dispatch send me one emergency service call, first in the morning i drove to site job upon arrival check-in with manager, then i located the case model RMN5MA, serial # MY26B016549, the case is a medium temperature and is a beer case, for next the controller on top of the case has one alarm E2 alarm which is related to the sensor, for next i set up my 6 foot ladder in order to open the controller box, then i found the defrost sensor S1, S2 wire lose in the terminal connection, i connected the wire sensor and connect the terminal wire back to the the controller, the case is not alarming for E2 sensor, and is working the case is set for 39 Fahrenheit cut-in and cut-out at 32 Fahrenheit, the termination defrost sensor is set for 48, and the termination defrost sensor, discharge air sensor, and the evaporator sensor, all this sensor are working, i set the unit in defrost test, and the refrigeration is working form 32 Fahrenheit and 39 Fahrenheit, for last i explain to the manager my performance and this call is complete. Resource: Juan Olvera Mendoza
37e83f7b-282d-f111-88b4-7c1e5257c290 | LRwgZeoi32phkmyAKdxdgwqjN+5GYfiRZEljduipTAV52ZmUoQgZswAhjUEnxoEBSrxHGc/E9sfYbP61c8/tWg== | 46132.6326 | 2026-03-31 10:39 |  | Posted | 2026-04-08 09:00 | WO-0542512 | Phoenix, AZ | Dollar General #16435 | Tuba City | AZ | 4894014 | FEXA | COMMUNICATION/STORE POWER ISSUE |  | X |  |  |  | BILLABLE CALL – READ DIRECTIONS BELOW – INVOICE TO DG.SERVICE@HUSSMANN.COM Hussmann Cases ONLY: Possible power surge/outage… Check all the existing/old Hussmann Cases to ensure operating correctly. Take picture and/or picture of equipment tag (model/serial) of each case you work on with detail summary. RFMN3 - MY20H061115 Lights keep flickering on and off and the temperature reads 12 degrees and increasing but drinks are still cold. been ongoing for awhile. RFMN4- MY20H061125- Lights keep flickering on and off and the temperature reads 67 degrees and rising but product is still cold. been ongoing for awhile. RFMN4- MY20H061124- Lights keep flickering on and off and the temperature reads 67 degrees and rising but product is still cold. been ongoing for awhile. RFMN4- MY20H061125- I was contacted by someone from Hussman Corporation and was asked to submit another ticket to try to get contact information for previous service technicians for older coolers but there is no other option and theres three old cooler units out and one new cooler unit out. Overtime Approved •Tech can work on multiple Hussmann Cases with one ticket, confirm all cases are operating or diagnose before leaving the store. •Tech must list or take pictures of the data tag of all equipment model/serial number repaired on service ticket and provide a detail work summary of each equipment repaired. •If you need assistance, please contact Hussmann Technical Support @ 800-922-1919, option #3. If Parts are needed, contact Hussmann Warranty Parts @ 855-487-7778, option #6 – state it’s for Dollar General •Copeland compressors are under warranty over the counter through United or Copeland Distributor. Sanhua TXV replacement is not available – source Sporlan. If parts are not available & have long lead time, send us an e-mail @ dg.service@hussmann.com to help locate. •Invoice MUST be submitted within 45 days of repair completion date to TAVANT. For support with warranty claim @ 800-398-7402, option #4 or hussmannwarrantyclaims@hussmann.com Send repair status with a brief work summary BEFORE leaving the location to dg.service@hussmann.com. If you have any questions, contact us at @ dg.service@hussmann.com Troubleshooting Process Step 1 - Start with documentation located within case · Operation Manual & Data Sheet with the case. Step 2 - Scan Hussmann QR Code located on model/serial plate · Type serial number of case and follow navigation for product sheets, data sheets, and manuals Step 3 – Scan BOX QR Code for Box account · Carries in depth support - parameters, controller guides etc. Step 4 - Contact technical support - direct line #866-785-8499 · Tech support will escalate to our Field Equipment Team if issue cannot be resolved – tech support does not provide NTE/OT approval | Insp coolers for not maintaining temp and found multiple coolers offline due to power issue. Found 1 leg of 3 phase power to not have power causing cases to flicker when trying to start. Verify dead power coming in and then cycle off all effected coolers. Asked to return after power restored. Inform store to contact aps to restore power Resource: Ryan Bugarin Complete. Resource: Ryan Bugarin
bafde50e-522c-f111-88b3-7c1e52ff753b | cLmL4e1l+TVzk3tkhHHNJHQd6AmdWN38pa4i2UDrHOurNT/3SVCfCrS00TQwSEnb9QGc+weOVewwkWCbHFsFqw== | 46135.0393 | 2026-03-30 09:04 |  | Completed | 2026-03-31 13:10 | WO-0541656 | Phoenix, AZ | DOLLAR GENERAL #10369 | Ajo | AZ | TAVANT/PRODUCT CARE HUS-1118022 | STORE CONNECT | WIRING/CONTROLLER |  |  |  | RMN5MA/MY26B016046, LEFT |  | Warranty end date: July 21, 2026 TECH must obtain a photo of the equipment tag that includes MODEL & SERIAL number on the CASE & CONDENSING UNIT (Tecumseh). Hussmann Equipment Dispatch Reason: High Temperature Alarm We are observing a High Temperature Alarm on the Serial number MY26B016046, Model: RMN5MA, LEFT microblock case at the above-mentioned location. The alarm has been active beyond the configured threshold of 60 minutes. The store is currently operational. If this condition is not addressed immediately, it may result in product loss, food safety risk, and significant store operational impact, potentially leading to customer dissatisfaction. To prevent any product loss and ensure continued store operations, we request an immediate P1 (Critical) level site visit. Tech – please review & confirm the check list items listed below: then contact "VIN" Vinodrajan Paramasivan/Store Connect via MS TEAMS when on site and before leaving the store. Checklist: • Inspect the evaporator coil for ice or frost accumulation • Verify the evaporator fan is active and running properly • Confirm airflow direction and un-obstructed air circulation • If ice is present: Perform a manual defrost to fully clear the evaporator coil • Verify Hot Gas Valve operation during defrosts • Confirm the condenser fan turns OFF during defrost • Verify the refrigerant charge level o If low, charge the system to the manufacturer-recommended level OT APPROVED – DURING STORES BUSINESS HOURS: 8am – 9pm (store will not stay past closing) Check In/Out with Store Manager on Duty Tech can work on multiple Hussmann Cases with one ticket, confirm all cases are operating or diagnose before leaving the store. Tech must list or take pictures of the data tag of all equipment model/serial number repaired on service ticket and provide a detail work summary of each equipment repaired. If you need assistance, please contact Hussmann Technical Support @ 800-922-1919, option #3. If Parts are needed, contact Hussmann Warranty Parts @ 855-487-7778, option #6 – state it’s for Dollar General Copeland compressors are under warranty over the counter through United or Copeland Distributor. Sanhua TXV replacement is not available – source Sporlan. If parts are not available & have long lead time, send us an e-mail @ dg.service@hussmann.com to help locate. Invoice MUST be submitted within 45 days of repair completion date to TAVANT. For support with warranty claim @ 800-398-7402, option #4 or hussmannwarrantyclaims@hussmann.com Send repair status with a brief work summary BEFORE leaving the location to dg.service@hussmann.com. If you have any questions, contact us at @ dg.service@hussmann.com | Check in with manager, tech found wire for c1 terminal on controller had become loose and was no longer connected, power off and secure wire to conecter and torque to spec. Start up unit and monitored operation untill setpoint. Perform checklist inspectio: no ice on evaporator, fan spinning correct direction, verify defrost operation as designed. Resource: Kelley Bruning
fc119d6e-462c-f111-88b3-7c1e52ff753b | 5c43lzlj5xVdv5rezLYRg3m8Dh9LOeDiapV7bbXEdG9mlvCDbDg40XRnfWQLkM9uFl3f+CZ5F2ltidQuSktrrw== | 46132.9681 | 2026-03-30 07:41 |  | Posted | 2026-04-09 08:41 | WO-0541572 | Tulsa, OK | Dollar General 22799 | Amarillo | TX | 4891201 | FEXA | ICE/FROST | PRODUCT LOSS - 2 LT |  |  | RLN2MA/MY26B014943 | YES | TECH must obtain a photo of the equipment tag that includes MODEL & SERIAL number on the CASE & CONDENSING UNIT (Tecumseh). We are observing a High Temperature Alarm on the Serial Hussmann Equipment Rln2ma- My26b014943- Temp to high OT APPROVED – DURING STORES BUSINESS HOURS: 8am – 9pm (store will not stay past closing) Check In/Out with Store Manager on Duty Tech can work on multiple Hussmann Cases with one ticket, confirm all cases are operating or diagnose before leaving the store. Tech must list or take pictures of the data tag of all equipment model/serial number repaired on service ticket and provide a detail work summary of each equipment repaired. If you need assistance, please contact Hussmann Technical Support @ 800-922-1919, option #3. If Parts are needed, contact Hussmann Warranty Parts @ 855-487-7778, option #6 – state it’s for Dollar General Copeland compressors are under warranty over the counter through United or Copeland Distributor. Sanhua TXV replacement is not available – source Sporlan. If parts are not available & have long lead time, send us an e-mail @ dg.service@hussmann.com to help locate. Invoice MUST be submitted within 45 days of repair completion date to TAVANT. For support with warranty claim @ 800-398-7402, option #4 or hussmannwarrantyclaims@hussmann.com Send repair status with a brief work summary BEFORE leaving the location to dg.service@hussmann.com. If you have any questions, contact us at @ dg.service@hussmann.com. arrived on site and spoke to store management. Proceeded to 2 door frozen case and saw case temperature display 16 degrees. Found that food in case had thawed out, informed manager. Began checking case and found fans operational. Saw that evaporator was completely iced up. Placed case in defrost and began searching for gaps in case that would lead to air infiltration. None found. Confirmed that defrost was operating. Was informed by manager that all product was to be thrown away so decided to turn case off and instructed staff how to turn case back on once coil thaws out after a couple days. Resource: Joseph Daum Turned unit back on let it get back down to set point going over case manuals found defrost term not set correctly and the set point not set correctly for frozen food adjusted once case was down to set point point into defrost watched over case hot gas defrost came on and temp jumped up to term and shut off watched temp get back down to set point Resource: Jake Hoppe | arrived on site and spoke to store management. Proceeded to 2 door frozen case and saw case temperature display 16 degrees. Found that food in case had thawed out, informed manager. Began checking case and found fans operational. Saw that evaporator was completely iced up. Placed case in defrost and began searching for gaps in case that would lead to air infiltration. None found. Confirmed that defrost was operating. Was informed by manager that all product was to be thrown away so decided to turn case off and instructed staff how to turn case back on once coil thaws out after a couple days. Resource: Joseph Daum Turned unit back on let it get back down to set point going over case manuals found defrost term not set correctly and the set point not set correctly for frozen food adjusted once case was down to set point point into defrost watched over case hot gas defrost came on and temp jumped up to term and shut off watched temp get back down to set point Resource: Jake Hoppe
ef7e2539-3c2c-f111-88b3-7c1e52ff753b | Tk8UucczaJhCREjSPveolWqui5hQVamDmO2n8dRdwQKoozB1D75o/+uVnbnMp6ZWgKnFkaZniDVvy0MjheyDrw== | 46141.9268 | 2026-03-30 06:28 | 5/15 Suzanne is waiting for Product Care team to respond | Send New Tech |  | WO-0541495 | Tulsa, OK | Dollar General #22149 | Anton | TX | TAVANT/PRODUCT CARE TIM SMITH | STORE CONNECT | COMMUNICATION | CAREL CONTROLLER |  |  | RMN5MA/MY26B013852 RLN3MA/MY26B013833 ~ RLN2MA/MY26B013807 ~ RFMN4/MY21G066701 |  | TECH must obtain a photo of the equipment tag that includes MODEL & SERIAL number on the CASE & CONDENSING UNIT (Tecumseh). Hussmann Equipment Store Connect-Pulse is not communicating, troubleshoot the network for resolution. Tech MUST contact "VIN" Vinodrajan Paramasivan/Store Connect via MS TEAMS when on site and before leaving the store. OT APPROVED – DURING STORES BUSINESS HOURS: 8am – 9pm (store will not stay past closing) Check In/Out with Store Manager on Duty Tech can work on multiple Hussmann Cases with one ticket, confirm all cases are operating or diagnose before leaving the store. Tech must list or take pictures of the data tag of all equipment model/serial number repaired on service ticket and provide a detail work summary of each equipment repaired. If you need assistance, please contact Hussmann Technical Support @ 800-922-1919, option #3. If Parts are needed, contact Hussmann Warranty Parts @ 855-487-7778, option #6 – state it’s for Dollar General Copeland compressors are under warranty over the counter through United or Copeland Distributor. Sanhua TXV replacement is not available – source Sporlan. If parts are not available & have long lead time, send us an e-mail @ dg.service@hussmann.com to help locate. Invoice MUST be submitted within 45 days of repair completion date to TAVANT. For support with warranty claim @ 800-398-7402, option #4 or hussmannwarrantyclaims@hussmann.com Send repair status with a brief work summary BEFORE leaving the location to dg.service@hussmann.com. If you have any questions, contact us at @ dg.service@hussmann.com | Arrived on site and spoke to management. Went to case and called store connect support Vinodrajan Paramasivan. checked all systems for proper addresses. All addresses correct. Checked wiring Across all cases and leading to store connect box. Wiring correct. Still only one case seen by store connect. Will have to return at later date to continue troubleshooting. All cases at operating temperatures. Resource: Joseph Daum Checked over com loop with Vin made sure all com loop connections are correct and tightened. Check all addresses on controllers. They are all correct. Determine that we have bad controllers and will get new controller shipped out. Resource: Jake Hoppe
0b15e0a8-3b2c-f111-88b3-7c1e52ff753b | ZSSPEA9gcXVYAeHasTAXtnPEtGCdQ/PBUU6NjcjFUuTPfddoi2GM76/9hckE7rkrDNKwChwI3SNQdk/Xe6cong== | 46134.6792 | 2026-03-30 06:24 |  | Posted | 2026-03-31 09:08 | WO-0541490 | Charlotte, NC | Dollar General #6099 | Newton | NC | TAVANT/PRODUCT CARE TIM SMITH | STORE CONNECT | COMMUNICATION |  |  |  | N/A |  | Warranty end date: July 14, 2026 TECH must obtain a photo of the equipment tag that includes MODEL & SERIAL number on the CASE & CONDENSING UNIT (Tecumseh). Hussmann Equipment Only Store Connect-Pulse is not communicating, troubleshoot the network for resolution. Tech MUST contact "VIN" Vinodrajan Paramasivan/Store Connect via MS TEAMS when on site and before leaving the store. OT APPROVED – DURING STORES BUSINESS HOURS: 8am – 9pm (store will not stay past closing) Check In/Out with Store Manager on Duty Tech can work on multiple Hussmann Cases with one ticket, confirm all cases are operating or diagnose before leaving the store. Tech must list or take pictures of the data tag of all equipment model/serial number repaired on service ticket and provide a detail work summary of each equipment repaired. If you need assistance, please contact Hussmann Technical Support @ 800-922-1919, option #3. If Parts are needed, contact Hussmann Warranty Parts @ 855-487-7778, option #6 – state it’s for Dollar General Copeland compressors are under warranty over the counter through United or Copeland Distributor. Sanhua TXV replacement is not available – source Sporlan. If parts are not available & have long lead time, send us an e-mail @ dg.service@hussmann.com to help locate. Invoice MUST be submitted within 45 days of repair completion date to TAVANT. For support with warranty claim @ 800-398-7402, option #4 or hussmannwarrantyclaims@hussmann.com Send repair status with a brief work summary BEFORE leaving the location to dg.service@hussmann.com. If you have any questions, contact us at @ dg.service@hussmann.com | Upon arrival to store checked in with MOD. Contacted Hussmann at 1-800-922-1919 #3. Talked with tech support. Tech support had Nate call me from Hussmann Missouri Store connect puluse team. Call me, reset store connect controller. Back on line. Meet James from Hussmann, Part of Dollar General team at store. Checked out with MOD. Call complete. Jbd. Resource: Joseph DeFranco
9e7b016e-fb29-f111-8341-6045bddb998a | IgpO1qNYo0fOMUSTe41pUPs048R2s+G1rScqVl5k7t8dcBK5zJzpkui3XpHQI1eO+q8rMDFYn8Z1zOP919Cohw== | 46112.6451 | 2026-03-27 09:39 |  | Completed | 2026-03-27 10:30 | WO-0540402 | RPM/Strategic Accounts | Dollar General #21135 | La Marque | TX | 4886013 | FEXA |  |  | X |  |  |  | Hussmann Cases ONLY: MY20C021319, Invalid temperature reading +60 non warranty billable STORES BUSINESS HOURS: 8am – 9pm (store will not stay past closing) Check In/Out with Store Manager on Duty, OBTAIN A SIGNATURE ON SERVICE TICKET & NOTE FIRST AND LAST NAME. Tech can work on multiple Hussmann Cases with one ticket, confirm all cases are operating or diagnose before leaving the store. Tech must list or take pictures of the data tag of all equipment model/serial number repaired on service ticket and provide a detail work summary of each equipment repaired. If you need assistance, please contact Hussmann Technical Support @ 800-922-1919, option #3. If Parts are needed, contact Hussmann Performance Parts @ 855-487-7778, press 1 for general inquiries. Confirm Copeland compressors are under warranty over the counter through United or Copeland Distributor. Sanhua TXV replacement is not available – source Sporlan. If parts are not available & have long lead time, send us an e-mail @ dg.service@hussmann.com to help locate. Invoice MUST be submitted within 30 days from date of repair completion to April Marolf @ april.marolf@hussmann.com and dg.service@hussmann.com. Send repair status with a brief work summary BEFORE leaving the location to dg.service@hussmann.com. If you have any questions, contact us at @ dg.service@hussmann.com | Techs onsite 3/30 completed Resource: CLIMATE COOL LLC
183455c4-4125-f111-8341-7c1e5257c75c | yESqzb61hOmh0kf63nvCEeeuoJBJQNoIkMd4kP32V36ngnR1bb1Jp4NU8OG0209WqzUdFYoKF6rLXXlcUBm2Fg== | 46126.8288 | 2026-03-21 09:20 |  | Completed | 2026-04-06 03:10 | WO-0536941 | Houston, TX | Dollar General #20582 | Houston | TX | TAVANT/PRODUCT CARE 4889009 | STORE CONNECT | TEMPERATURE ALARM | CONDENSING UNIT |  |  | RLN3MA/MY26B014956, LEFT ~ RLN2MA/ MY26B016476, LEFT |  | UPDATE: 3/22: another case RLN3MA/MY26B014956, left condensing unit appears to be having an issue. Priority: P1 – Critical (Immediate) Sorry - change: Tech must contact "VIN" Vinodrajan Paramasivan/Store Connect via TEAMS, when on site and before leaving the store. Dispatch Reason: High Temperature Alarm We are observing a High Temperature Alarm on the Serial number MY26B016476, Model: RLN2MA, LEFT microblock case at the above-mentioned location. The alarm has been active beyond the configured threshold of 60 minutes. The store is currently operational. If this condition is not addressed immediately, it may result in product loss, food safety risk, and significant store operational impact, potentially leading to customer dissatisfaction. To prevent any product loss and ensure continued store operations, we request an immediate P1 (Critical) level site visit. Checklist: • Inspect the evaporator coil for ice or frost accumulation • Verify the evaporator fan is active and running properly • Confirm airflow direction and un-obstructed air circulation • If ice is present: Perform a manual defrost to fully clear the evaporator coil • Verify Hot Gas Valve operation during defrosts • Confirm the condenser fan turns OFF during defrost • Verify the refrigerant charge level o If low, charge the system to the manufacturer-recommended level | 3/21/26 I arrive in spoke with the manager. Found the location of the moisture in the entering the case. Washed the evaporator. Was not able to wash the backside of the evaporator, will let thaw out overnight and return in the morning to start the case back up. Resource: Thomas Waid 3/22/26 I arrived and spoke with the manager. Reassembled the case, fastening the ceiling panels to the canopy, setting in place: the shelves and lower deck pans. Removed the water that drained into the drain pan, whilst the case was powered down, using a wet vacuum. Sealed around the cassette with foam-o-fil, to prohibit moisture from entering in through gaps. Started it up the case, and it is pulling down to temperature setpoint. Currently it's at minus 1 degree fahrenheit. Was told to investigate the adjacent 3 door self contained freezer. Found that the evaporator needs to be defrosted. Spoke with the manager, they asked me to return tomorrow to power down the case after the product has been pulled. Cleaned up the area and picked up all trash. Resource: Thomas Waid Arrived, checked i. With the manager, spoke with the field engineer, verified the evaporators had defrosted, verified slope on the drain lines, applied foam-o-fil to the front most edge of the cassete housing for both evaporators. Started up the unit. Will return tomorrow to finish up Resource: Thomas Waid 3/25/26 I arrived and checked in with the manager. Worked on finding installation issues with the hussmann field engineer Resource: Thomas Waid 3/26/26 I arrived and spoke with the manager. Did time tables of the line temperatures during defrost, took amperages of the solenoids during defrost. Helped the field engineer collect the information. Currently both cases are hovering around temperature setpoint. Informed the manager it was safe to put the product back. Resource: Thomas Waid 3/27/26 I arrived and spoke with the manager. Helped the field engineer run tests, had the product pulled from the two door freezer and moved the three door freezer. Disconnected the power to the unit(two door), will return Monday to add propane to the two door unit. Resource: Thomas Waid 3/30/26 Leak tested self contained unit. Cassette, atop unit to be replaced. Part is being sent by the factory. Will replace cassette after it arrives. Resource: Thomas Waid Assisted tech on site Resource: Marques Pierre-Louis case unit Resource: Devin Scott 4/2/26 I pucked up the replacement cassette. I arrived and spoke with the manager. Installed the replacement cassette. Applied butly-sealant around the all three cassettes: the newly replaced cassette and around the two on the unit that had not been replaced. Took amperage measurements for the new cassette during defrost, the amps indicate the unit has a full charge of propane. Took temperature measurements for the new cassette during defrost, the temperature readings verify that the unit is reaching the critical pressure needed to defrost the evaporator coil during defrost. Tested the case itself for leaks in its seals using a fog machine, no leaks. Currently the case is at minus 2 degrees Fahrenheit and pulling down to temperature setpoint. Cleaned up the work area and picked up all trash. Informed the manager to leave the freezer unstocked tonight and that they would be able to use the freezer tomorrow, and they are aware. Cassette Model# ALX44OU-DS3B01 Serial# 04C1726120983 Resource: Thomas Waid
d90c8094-8524-f111-8341-000d3a1d8d04 | 4iq7Qu+3ysAqeDYw3jArmoLgpbBcxrj5ieWGCEkPIhV58Txnfaw7+qQOKn2SpdI6POZkTNr1Mq8gUMOEIGc0RQ== | 46113.7528 | 2026-03-20 10:53 |  | Posted | 2026-03-26 20:02 | WO-0536554 | Gulf | Dollar General #31793 | Clay | AL | 4861471 | FEXA | ASSESSMENT |  | X |  | RFMN5/MY20D029393 |  | This is a billable/FEXA (existing Hussmann Equipment) call & ignore the NTE amount; Perform a thorough inspection of the problem case(s). submit a proposal for repairs that require parts to be ordered. Tech can proceed if parts are available on his truck, if not – must pull off & submit proposal for approval to proceed. Please note it doesn’t matter someone else install the cases & are Hussmann cases. Warranty end date: July 4, 2026 Hussmann Cases ONLY: my20d029393, Not keeping the specified temperature, Not working at all . my20c024328, There is a strong smell inside the unit. OT APPROVED – DURING STORES BUSINESS HOURS: 8am – 9pm (store will not stay past closing) Check In/Out with Store Manager on Duty Tech can work on multiple Hussmann Cases with one ticket, confirm all cases are operating or diagnose before leaving the store. Tech must list or take pictures of the data tag of all equipment model/serial number repaired on service ticket and provide a detail work summary of each equipment repaired. If you need assistance, please contact Hussmann Technical Support @ 800-922-1919, option #3. If Parts are needed, contact Hussmann Warranty Parts @ 855-487-7778, option #6 – state it’s for Dollar General Copeland compressors are under warranty over the counter through United or Copeland Distributor. Sanhua TXV replacement is not available – source Sporlan. If parts are not available & have long lead time, send us an e-mail @ dg.service@hussmann.com to help locate. Invoice MUST be submitted within 45 days of repair completion date to TAVANT. For support with warranty claim @ 800-398-7402, option #4 or hussmannwarrantyclaims@hussmann.com Send repair status with a brief work summary BEFORE leaving the location to dg.service@hussmann.com. If you have any questions, contact us at @ dg.service@hussmann.com | My20d029393 case was at temp, freezer case no issue My20c024328 smell, this was in all case but it's not out of the ordinary for older equipment to have an oder. This case also has 1 fan motor out was going to pick up new motor and installed on Wednesday the 25th of March, was told by store that was the next day someone would be on site. Jared wants to qoute a coil cleaning on the cases My20c018770 was the only case not at temp, medium temp case, suspected low on gas, added 3 lbs of 448a to case and case was below 38 degrees at time of departure. Both king valve caps and service port caps were loose leaking small amount of refrigerant. All other cases were running without issue Resource: Andrew Harp Went by united in the way to site and picked up new fan motor for first case. Once arrived at site removed lower panel and took fan assembly out. Changed out motor and reinstalled. Also picked up some odor neutralize spray form. Went through each medium temp case and sprayed length of case to remove smell. Leak checked back over case that gas was added to, no leaks found. 2 cases were in alarm but it was due to vendors adding product. No other issues found. *parts only used 1 of 2 motors used, wouldn't allow to only fulfill 1. Resource: Andrew Harp
431e73b2-8324-f111-8341-000d3a1d8d04 | len/p2+Gpmgi1BHcE0z2mYLafOvBqo6Rn6D2/WPtq5qWPRiFLNsO3wayaYRtc61YtzRIJlwfGvGBmV4CLz8LoA== | 46140.7112 | 2026-03-20 10:39 |  | Posted | 2026-04-26 18:04 | WO-0536547 | Charlotte, NC | Dollar General 25565 | Norton | VA | 4869761 | FEXA | ASSESSMENT |  | X |  |  |  | THIS IS A BILLABLE CALL - Perform a thorough assessment of all the Hussmann Equipment, cases are out of warranty; installed back in March 2023, 3 years old. Take pictures of the cases, check the store temperature, ambient conditions & quote repairs needed. Hussmann Cases ONLY: this location's entire lineup is down currently . We need a Hussmann technician to assist with completing an assessment and quote what will get us back up and running . Candace Robertson SSC STORES BUSINESS HOURS: 8am – 9pm (store will not stay past closing) Check In/Out with Store Manager on Duty, OBTAIN A SIGNATURE ON SERVICE TICKET & NOTE FIRST AND LAST NAME. Tech can work on multiple Hussmann Cases with one ticket, confirm all cases are operating or diagnose before leaving the store. Tech must list or take pictures of the data tag of all equipment model/serial number repaired on service ticket and provide a detail work summary of each equipment repaired. If you need assistance, please contact Hussmann Technical Support @ 800-922-1919, option #3. If Parts are needed, contact Hussmann Performance Parts @ 855-487-7778, press 1 for general inquiries. Confirm Copeland compressors are under warranty over the counter through United or Copeland Distributor. Sanhua TXV replacement is not available – source Sporlan. If parts are not available & have long lead time, send us an e-mail @ dg.service@hussmann.com to help locate. Invoice MUST be submitted within 30 days from date of repair completion to April Marolf @ april.marolf@hussmann.com and dg.service@hussmann.com. Send repair status with a brief work summary BEFORE leaving the location to dg.service@hussmann.com. If you have any questions, contact us at @ dg.service@hussmann.com | Did thorough assessment of frozen and refrigerated equipment. Found all condensers covered in debris from fire extingushers. Found drains clogged and freezers full of water. Found 1 bad blue diamond condenstae pump. One bad heated condensate pan. Several units were oil and need to be leakk tested. Sight glasses were low on some of the units as weĺl. Resource: Steven Marshall Did thorough assessment of frozen and refrigerated equipment. Found all condensers covered in debris from fire extingushers. Found drains clogged and freezers full of water. Found 1 bad blue diamond condenstae pump. One bad heated condensate pan. Several units were oil and need to be leakk tested. Sight glasses were low on some of the units as weĺl. Resource: Steven Marshall Assisted Logan Hagood Resource: Dylan Yates . Resource: Austin Artrip Completed by Austin Artrip and Steve Marshall Resource: Dylan Yates Finished cleaning condensers and installed pump. Found another pump bad for a total of 3. Sent Suzanne Basaca email and informed her of eta on parts and completion date on store. 4/!5- Arrived on site and installed heated pans. Made sure everything was working properly. Will return on opening morning per managers request. will return Call has been completed. Resource: Steven Marshall Complete Resource: Kenneth Hagood
3f0bfbb9-cd23-f111-8341-7c1e52820356 | u8Ne2bfmtmSyI4i3XgTpw+vUZ7B1vzG691MT4ZDOyzpEIwW6I+dUfRsID1uvl1k3G7jROEXHZ3QDREWQX2j0aQ== | 46108.9253 | 2026-03-19 12:57 |  | Posted | 2026-03-19 16:33 | WO-0536090 | Houston, TX | Dollar General #04117 | Alvin | TX | TAVANT/TIM SMITH | TIM SMITH | COMMUNICATION | [5 empty] | Warranty end date: Hussmann Cases ONLY: New Hussmann R290 Cases are DOWN. Tech must contact Tim Smith/Sales Rep @ 479-502-4290 when on site & before leaving! Or he will reach out to you. OT APPROVED – DURING STORES BUSINESS HOURS: 8am – 9pm (store will not stay past closing) Check In/Out with Store Manager on Duty Tech can work on multiple Hussmann Cases with one ticket, confirm all cases are operating or diagnose before leaving the store. Tech must list or take pictures of the data tag of all equipment model/serial number repaired on service ticket and provide a detail work summary of each equipment repaired. If you need assistance, please contact Hussmann Technical Support @ 800-922-1919, option #3. If Parts are needed, contact Hussmann Warranty Parts @ 855-487-7778, option #6 – state it’s for Dollar General Copeland compressors are under warranty over the counter through United or Copeland Distributor. Sanhua TXV replacement is not available – source Sporlan. If parts are not available & have long lead time, send us an e-mail @ dg.service@hussmann.com to help locate. Invoice MUST be submitted within 45 days of repair completion date to TAVANT. For support with warranty claim @ 800-398-7402, option #4 or hussmannwarrantyclaims@hussmann.com Send repair status with a brief work summary BEFORE leaving the location to dg.service@hussmann.com. If you have any questions, contact us at @ dg.service@hussmann.com | Meet with installation contractor and checked new cases. Cases were not comming online in their ems system. Checked comm wiring, ran new comm wire and verified polarity, polarity in carell case controller was at the wrong connections points, corrected and , tested out , now all case controllers are online and all temperatures are normal.. Resource: German Castillo
b7bb1362-f91e-f111-8341-6045bddb9d4c | yt0SLX323Rcg0Z1h3CeV8C8fwcenfHG0cgZqenzr6LpQ1zcMy8BeAhTND3S37vRZo5aKlFFOPO8twUu5ykzMSQ== | 46106.8508 | 2026-03-13 09:26 |  | Posted | 2026-03-13 14:08 | WO-0532764 | Tulsa, OK | Dollar General #22515 | Fort Smith | AR | 4847185 | FEXA | WATER LEAK |  |  |  | RMN5MA/MY26B013859 | YES | Warranty end date: June 30, 2026 Hussmann Cases ONLY: RMN5MA, MY26B013859 there is water dripping from top inside the cooler, shelves have water standing and product is getting soaked. There is also a few doors that will not close right back they will stay open unless you force to close. OT APPROVED – DURING STORES BUSINESS HOURS: 8am – 9pm (store will not stay past closing) Check In/Out with Store Manager on Duty Tech can work on multiple Hussmann Cases with one ticket, confirm all cases are operating or diagnose before leaving the store. Tech must list or take pictures of the data tag of all equipment model/serial number repaired on service ticket and provide a detail work summary of each equipment repaired. If you need assistance, please contact Hussmann Technical Support @ 800-922-1919, option #3. If Parts are needed, contact Hussmann Warranty Parts @ 855-487-7778, option #6 – state it’s for Dollar General Copeland compressors are under warranty over the counter through United or Copeland Distributor. Sanhua TXV replacement is not available – source Sporlan. If parts are not available & have long lead time, send us an e-mail @ dg.service@hussmann.com to help locate. Invoice MUST be submitted within 45 days of repair completion date to TAVANT. For support with warranty claim @ 800-398-7402, option #4 or hussmannwarrantyclaims@hussmann.com Send repair status with a brief work summary BEFORE leaving the location to dg.service@hussmann.com. If you have any questions, contact us at @ dg.service@hussmann.com. Arrived on site and checked in. Cooler leaking water onto product. Also doors not closing. Adjusted torque rods on doors and this resolved the closing issue. Doors now closing normally. Both self evaporation condesnate pans on cooler units bone dry and water building up in evaporator overflowing and dripping into product. Checked drain lines for blockages. Opened doors to break air vacuum and drains started working. Reached out to Jeff Fosnaugh and he met me here on site to go over issue. Could be a leak or possible issue with negative pressure in evaporator causing water not to drain. Jeff is going to return to site on monday to see if issue is persistent and is unit needs to be replaced. Will leave ticket open and will talk to jeff on monday on how to proceed with WO. Resource: Neil Sparks | Arrived on site and checked in. Cooler leaking water onto product. Also doors not closing. Adjusted torque rods on doors and this resolved the closing issue. Doors now closing normally. Both self evaporation condesnate pans on cooler units bone dry and water building up in evaporator overflowing and dripping into product. Checked drain lines for blockages. Opened doors to break air vacuum and drains started working. Reached out to Jeff Fosnaugh and he met me here on site to go over issue. Could be a leak or possible issue with negative pressure in evaporator causing water not to drain. Jeff is going to return to site on monday to see if issue is persistent and is unit needs to be replaced. Will leave ticket open and will talk to jeff on monday on how to proceed with WO. Resource: Neil Sparks
b1be78fc-871d-f111-8341-7c1e5257c290 | Sb9b19hspP2ZOd2Bq4JfDRA0MqWfO5duAJrlnjnVob7Ayvnv6WTE399TZdVItIL4u1X5S9F/l6/Y3ZPTti3teg== | 46141.7556 | 2026-03-11 13:22 |  | Posted | 2026-03-15 22:48 | WO-0531599 | Phoenix, AZ | Dollar General #25554 | Congress | AZ | 4829112 | FEXA | TEMPERATURE |  | X |  | RFLN3/MY24D034504 |  | Hussmann Cases ONLY: RFLN3/MY24D034504 Invalid Temperature – tech must thoroughly check & repair case. If technical support is needed, please call 800-922-1919; option #3 or FER Team: Todd Green @ 210-346-0005, Jeff Fosnaugh @ 314-501-8736 or Andrew Miller @ 314-501-8698. OT APPROVED – DURING STORES BUSINESS HOURS: 8am – 9pm (store will not stay past closing) Check In/Out with Store Manager on Duty Tech can work on multiple Hussmann Cases with one ticket, confirm all cases are operating or diagnose before leaving the store. Tech must list or take pictures of the data tag of all equipment model/serial number repaired on service ticket and provide a detail work summary of each equipment repaired. If you need assistance, please contact Hussmann Technical Support @ 800-922-1919, option #3. If Parts are needed, contact Hussmann Warranty Parts @ 855-487-7778, option #6 – state it’s for Dollar General Copeland compressors are under warranty over the counter through United or Copeland Distributor. Sanhua TXV replacement is not available – source Sporlan. If parts are not available & have long lead time, send us an e-mail @ dg.service@hussmann.com to help locate. Invoice MUST be submitted within 45 days of repair completion date to TAVANT. For support with warranty claim @ 800-398-7402, option #4 or hussmannwarrantyclaims@hussmann.com Send repair status with a brief work summary BEFORE leaving the location to dg.service@hussmann.com. If you have any questions, contact us at @ dg.service@hussmann.com | Hussmann frozen case running warm. Model # RFLN3 Serial # MY24D034504. Manufacture date 4/22/24 not sure if case is under warranty. Tried calling tech support for warranty info and they were closed for the night. Did not work on case until further notice. Resource: Ramond Ramirez Arrived on site, checked in with manager. Found 3 door freezer low or gas leaking from a loose compression fitting. Tightened fitting and stopped leak. Added 3 lbs of R-448A and monitored system operation and pressure while it dropped in temp. We are now running at proper temp with 7°F of superheat and 11°F of subcool. All operations in the green. Resource: Christian Billingsley
d0abe02a-5d1d-f111-8341-000d3a9c89ad | wn9InjAQwcPnVR8AdWsXr/msSfac5ynnq4ausAwaMKRbBJvPj6DIFq55vjKUhppUaDpE6pV3DSEGT1uN9P+AOw== | 46106.8445 | 2026-03-11 08:16 |  | Posted | 2026-03-11 14:27 | WO-0531272 | Tulsa, OK | Dollar General #21606 | Porum | OK | TAVANT/4838996 | FEXA | WATER LEAK |  |  |  | RMN5MA/MY26B013853 | YES | Warranty end date: June 30, 2026 Hussmann Cases ONLY: RMN5MA, MY26B013853 Water is leaking under unit, The cooler is leaking a fair amount of water out of the bolt that connects the door to the rest of the machine. The water is leaking down the entirety of the inside of the door with no clear sign of it stopping. The bolt seems to be loos OT APPROVED – DURING STORES BUSINESS HOURS: 8am – 9pm (store will not stay past closing) Check In/Out with Store Manager on Duty Tech can work on multiple Hussmann Cases with one ticket, confirm all cases are operating or diagnose before leaving the store. Tech must list or take pictures of the data tag of all equipment model/serial number repaired on service ticket and provide a detail work summary of each equipment repaired. If you need assistance, please contact Hussmann Technical Support @ 800-922-1919, option #3. If Parts are needed, contact Hussmann Warranty Parts @ 855-487-7778, option #6 – state it’s for Dollar General Copeland compressors are under warranty over the counter through United or Copeland Distributor. Sanhua TXV replacement is not available – source Sporlan. If parts are not available & have long lead time, send us an e-mail @ dg.service@hussmann.com to help locate. Invoice MUST be submitted within 45 days of repair completion date to TAVANT. For support with warranty claim @ 800-398-7402, option #4 or hussmannwarrantyclaims@hussmann.com Send repair status with a brief work summary BEFORE leaving the location to dg.service@hussmann.com. If you have any questions, contact us at @ dg.service@hussmann.com | Arrived on site and checked in. Cooler leaking water. Found condesnate line blocked due to aluminum tape being damaged causing water to build up in evaporator. Fixed this issue. All other self evaporation pans were almost full of water and store is very humid. Informed manager that high humidity can causing excessive water in pans. All equipment is operational and draining, evaporating normally. Issue resolved. Resource: Neil Sparks
51dbb896-b61c-f111-8341-70a8a5462361 | lj/1jGbsad4GoEHJslmowQbJsZoURJhD4v64jtNgHX2Iv3pxP6JL5FsgUvV2iMTBYYM1vBOi40JWb/FB4ZcvmQ== | 46097.7547 | 2026-03-10 12:23 |  | Completed | 2026-03-11 06:00 | WO-0530734 | RPM/Strategic Accounts | Dollar General #23669 | Falls City | TX | 4834020 | FEXA |  |  | X |  |  |  | Hussmann Cases ONLY: Serial #MY21M107766 - Invalid temp reading @ 60 degrees OT APPROVED – DURING STORES BUSINESS HOURS: 8am – 9pm (store will not stay past closing) Check In/Out with Store Manager on Duty Tech can work on multiple Hussmann Cases with one ticket, confirm all cases are operating or diagnose before leaving the store. Tech must list or take pictures of the data tag of all equipment model/serial number repaired on service ticket and provide a detail work summary of each equipment repaired. If you need assistance, please contact Hussmann Technical Support @ 800-922-1919, option #3. If Parts are needed, contact Hussmann Warranty Parts @ 855-487-7778, option #6 – state it’s for Dollar General Copeland compressors are under warranty over the counter through United or Copeland Distributor. Sanhua TXV replacement is not available – source Sporlan. If parts are not available & have long lead time, send us an e-mail @ dg.service@hussmann.com to help locate. Invoice MUST be submitted within 45 days of repair completion date to TAVANT. For support with warranty claim @ 800-398-7402, option #4 or hussmannwarrantyclaims@hussmann.com Send repair status with a brief work summary BEFORE leaving the location to dg.service@hussmann.com. If you have any questions, contact us at @ dg.service@hussmann.com | Good morning, on Thursday the 12th we went to the store and replaced the compressor fan on model: RFMN5 - MY21M107766 and it worked perfectly Resource: CLIMATE COOL LLC
58eb6681-4d16-f111-8341-7c1e5257c75c | DNawoT93gzfncNVzCryAJQazFndTXjyAZ5YsD1446ymHxamOzkPU7Mb7l18Ob4UX4jqyPAblNR1eOmNi4JQINw== | 46135.0419 | 2026-03-02 07:36 |  | Completed | 2026-03-02 08:30 | WO-0524098 | RPM/Strategic Accounts | Dollar General #23669 | Falls City | TX | 4813913 | FEXA |  |  | X |  |  |  | BILLABLE CALL – READ DIRECTIONS BELOW Warranty end date: (June 23,2026) Hussmann Cases ONLY: < RFLN4 - MY20D029035 - ICE CREAM COOLER IS NOT WORKING OR KEEPING TEMP. THE TEMP IS CURRENTLY READING AT 12 DEGREES. AND ICE CREAM BOXES ARE GETTING SOFT.- RFMN5 - MY21M107766 - NEW COOLERS WERE PUT IN AND THE COOLERS WITH THE MILK IS NOT KEEPING TEMP. IT IS KEEPING THE MILK COOL BUT NOT COLD AND IT IS READING A TEMP OF 57 DEGREES. > STORES BUSINESS HOURS: 8am – 9pm (store will not stay past closing) Check In/Out with Store Manager on Duty, OBTAIN A SIGNATURE ON SERVICE TICKET & NOTE FIRST AND LAST NAME. Tech can work on multiple Hussmann Cases with one ticket, confirm all cases are operating or diagnose before leaving the store. Tech must list or take pictures of the data tag of all equipment model/serial number repaired on service ticket and provide a detail work summary of each equipment repaired. If you need assistance, please contact Hussmann Technical Support @ 800-922-1919, option #3. If Parts are needed, contact Hussmann Performance Parts @ 855-487-7778, press 1 for general inquiries. Confirm Copeland compressors are under warranty over the counter through United or Copeland Distributor. Sanhua TXV replacement is not available – source Sporlan. If parts are not available & have long lead time, send us an e-mail @ dg.service@hussmann.com to help locate. Invoice MUST be submitted within 45 days from date of repair completion to April Marolf @ april.marolf@hussmann.com and dg.service@hussmann.com. Send repair status with a brief work summary BEFORE leaving the location to dg.service@hussmann.com. If you have any questions, contact us at @ dg.service@hussmann.com DISPATCH Below are the details for a new service call. BILLABLE CALL – READ DIRECTIONS BELOW – INVOICE TO DG.SERVICE@HUSSMANN.COM o Site Name/#: Dollar General o Address: o Store Hours: 8am – 9pm (store will not stay past closing) o NTE: Cannot exceed $1500 (including sales tax & freight). Proposal for increase must be submitted before the work is done. o PO: o Problem: Check In/Out with Store Manager on Duty Hussmann Equipment ONLY: <insert issue> · Tech can work on multiple Hussmann Cases with one ticket, confirm all cases are operating or diagnose before leaving the store. · Tech must list or take pictures of the data tag of all equipment model/serial number repaired on service ticket and provide a detail work summary of each equipment repaired. · If you need assistance, please contact Hussmann Technical Support @ 800-922-1919, option #3. If Parts are needed, contact Hussmann Warranty Parts @ 855-487-7778, option #6 – state it’s for Dollar General · Copeland compressors are under warranty over the counter through United or Copeland Distributor. Sanhua TXV replacement is not available – source Sporlan. If parts are not available & have long lead time, send us an e-mail @ dg.service@hussmann.com to help locate. · Invoices must be submitted within 45 days of repair completion date through FEXA for payment. Reach out to April Marolf with any questions. Send repair status with a brief work summary BEFORE leaving the location to dg.service@hussmann.com. If you have any questions, contact us at @ dg.service@hussmann.com Troubleshooting Process Step 1 - Start with documentation located within case · Operation Manual & Data Sheet with the case. Step 2 - Scan Hussmann QR Code located on model/serial plate · Type serial number of case and follow navigation for product sheets, data sheets, and manuals Step 3 – Scan BOX QR Code for Box account · Carries in depth support - parameters, controller guides etc. Step 4 - Contact technical support - direct line #866-785-8499 · Tech support will escalate to our Field Equipment Team if issue cannot be resolved – tech support does not provide NTE/OT approval | We work on the 3-door freezer, Model RFL 4 Serial # MY20D029035 We replaced a damaged contactor; I'll be attaching photos. The job was completed successfully. Resource: CLIMATE COOL LLC
4b89cb41-e215-f111-8341-7c1e5257ceaa | IDn+podOq3bkeLb7H52ZXt5H2xbq1SR9cIpFNKhCxW4RWfXXsrzoT5Mf1+iYZn0j6q+tJK9C59XupzJtsbpz6A== | 46118.0213 | 2026-03-01 18:48 |  | Completed | 2026-03-04 15:00 | WO-0522796 | RPM/Strategic Accounts | Dollar General #13736 | Beeville | TX | 4812073 | FEXA |  |  | X |  |  |  | BILLABLE CALL – READ DIRECTIONS BELOW – INVOICE TO FEXA Warranty end date: 6/23/2026 Hussmann Cases ONLY: MY20E035123 Temp is reading 58 and lights are blinking and it appears coolers turning off and on. // MY20E035123 Invalid temp reading +62°. // MY20E039971 Invalid temp reading +68°. // STORES BUSINESS HOURS: 8am – 9pm (store will not stay past closing) Check In/Out with Store Manager on Duty, OBTAIN A SIGNATURE ON SERVICE TICKET & NOTE FIRST AND LAST NAME. Tech can work on multiple Hussmann Cases with one ticket, confirm all cases are operating or diagnose before leaving the store. Tech must list or take pictures of the data tag of all equipment model/serial number repaired on service ticket and provide a detail work summary of each equipment repaired. If you need assistance, please contact Hussmann Technical Support @ 800-922-1919, option #3. If Parts are needed, contact Hussmann Performance Parts @ 855-487-7778, press 1 for general inquiries. Confirm Copeland compressors are under warranty over the counter through United or Copeland Distributor. Sanhua TXV replacement is not available – source Sporlan. If parts are not available & have long lead time, send us an e-mail @ dg.service@hussmann.com to help locate. Invoice MUST be submitted within 45 days from date of repair completion to April Marolf @ april.marolf@hussmann.com and dg.service@hussmann.com. Send repair status with a brief work summary BEFORE leaving the location to dg.service@hussmann.com. If you have any questions, contact us at @ dg.service@hussmann.com | Tech on site. Electrician needed. Resource: ENCORE MECHANICAL LLC Call completed Resource: ENCORE MECHANICAL LLC
cc93cb6e-d515-f111-8341-7c1e5257ceaa | rirjq/Z7LsRORQsViD4YlwS6IKBB8z5zmsEEp3eDskLAmM6As5eZ0/AdNWw/j0ewdUlW5EOhmYqOfTkF+2LB6A== | 46092.7297 | 2026-03-01 17:16 |  | Posted | 2026-03-04 10:31 | WO-0522756 | Gulf | Dollar General #20467 | Slidell | LA | 4811927 | FEXA | ICE/FROST |  | X |  | RFMN5/MY19M090252 |  | MY19M090252 Not keeping cool and alarm is sounding temp is at 60 BILLABLE CALL – READ DIRECTIONS BELOW – INVOICE TO FEXA Warranty end date: 5/19/2026 Hussmann Cases ONLY: MY19F050586 Unit is leaking water. STORES BUSINESS HOURS: 8am – 9pm (store will not stay past closing) Check In/Out with Store Manager on Duty, OBTAIN A SIGNATURE ON SERVICE TICKET & NOTE FIRST AND LAST NAME. Tech can work on multiple Hussmann Cases with one ticket, confirm all cases are operating or diagnose before leaving the store. Tech must list or take pictures of the data tag of all equipment model/serial number repaired on service ticket and provide a detail work summary of each equipment repaired. If you need assistance, please contact Hussmann Technical Support @ 800-922-1919, option #3. If Parts are needed, contact Hussmann Performance Parts @ 855-487-7778, press 1 for general inquiries. Confirm Copeland compressors are under warranty over the counter through United or Copeland Distributor. Sanhua TXV replacement is not available – source Sporlan. If parts are not available & have long lead time, send us an e-mail @ dg.service@hussmann.com to help locate. Invoice MUST be submitted within 45 days from date of repair completion to April Marolf @ april.marolf@hussmann.com and dg.service@hussmann.com. Send repair status with a brief work summary BEFORE leaving the location to dg.service@hussmann.com. If you have any questions, contact us at @ dg.service@hussmann.com | Travel to site and check in with Wil .Locate deli case iced up and have case uloaded.. Additional Work Resource: Christopher Casanovas Travel back to site and deli case has thawed ,with normal air flow.Check pressure temperature and case has enough refrigerant.Note that case temperature sensor and test digital instrument are off .Dixell case sensor is off and make a justment via Hussmann tech support.Also check and adjusted case superheat.Log store Emerson controler and case never reached target temperature 32 as far back as January. Witness case reach target temperature 32 and cycle back on at 38.Case is back to normal operation. Check frozen pizza case and it had air leak causing drip on right side.Seal joining seam with air breach .Use foil gum tape preventing air penetration. Resource: Christopher Casanovas
4004f35f-b915-f111-8341-7c1e5257ceaa | 1ZqQIdsU0fLzsyK4Nc6uQVCmtIt/BhtvMR+ECyWlrvr4AlcV24ToAR/iqO+zQDrdxGQSH9UCdDJaRjlIaZL1rg== | 46108.8897 | 2026-03-01 13:56 |  | Completed | 2026-03-24 09:38 | WO-0522685 | Des Moines, IA (Urbandale) | Dollar General #7398 | Marion | IA | 4812464 | FEXA |  |  | X |  |  |  | BILLABLE CALL – READ DIRECTIONS BELOW – INVOICE TO FEXA Warranty end date: 6/23/2026 Hussmann Cases ONLY: MY19K071633 The cooler temp is at 80 degrees and reading a CA code. and there is an alarm going off as well. STORES BUSINESS HOURS: 8am – 9pm (store will not stay past closing) Check In/Out with Store Manager on Duty, OBTAIN A SIGNATURE ON SERVICE TICKET & NOTE FIRST AND LAST NAME. Tech can work on multiple Hussmann Cases with one ticket, confirm all cases are operating or diagnose before leaving the store. Tech must list or take pictures of the data tag of all equipment model/serial number repaired on service ticket and provide a detail work summary of each equipment repaired. If you need assistance, please contact Hussmann Technical Support @ 800-922-1919, option #3. If Parts are needed, contact Hussmann Performance Parts @ 855-487-7778, press 1 for general inquiries. Confirm Copeland compressors are under warranty over the counter through United or Copeland Distributor. Sanhua TXV replacement is not available – source Sporlan. If parts are not available & have long lead time, send us an e-mail @ dg.service@hussmann.com to help locate. Invoice MUST be submitted within 45 days from date of repair completion to April Marolf @ april.marolf@hussmann.com and dg.service@hussmann.com. Send repair status with a brief work summary BEFORE leaving the location to dg.service@hussmann.com. If you have any questions, contact us at @ dg.service@hussmann.com WO Summary 3/1/26- arrived on site and got checked in with management and found out the case started running warm yesterday. He showed me the case that was running warm, they removed product before having to throw away. I found the E2 in the back room but do not have the user name and password to clear the alarms on the case. I couldn't get ahold of anyone who knew who Installed this case or who knew what the username/password is. I verified all evap fans were running, they are. I got on top of the case and found the condensing unit. I pulled the cover off the compressor and found it didn't have voltage going to it so it was wasn't being told to run. I tried to reset the dizell controller on top of the case but it was locked out with an alarm "CA" and wouldn't allow me to make any adjustments. I talked with management and they agreed for me to come back in the morning when I can get more information on the unit and the log in information for fhe E2 controller. He agreed. 3/2/26- got ahold of my service manager this morning and gave him the information on the service call and store. He found out that hussmann did not install the cases and so he couldn't get the log in information for me. He also found out that the cases were not under warranty. I arrived on site and got checked in with management. I informed them that we did not install these hussmann cases and that they are not under warranty since they are refurbished and not brand new. They agreed to have me work on the case anyways. I called hussmann tech support and he was able to help me pull up the system on the E2 and check to see if it was online and communicating. We ended up finding it was offline, and the dixxel controller was not communicating with the E2, therefore the compressor wasn't being told to run. I had to reset the system and get the two controllers back online and communicating. Once I did that the condensing unit kicked on and the case began cooling down. I watched it get down to 40 before leaving. Going to let it run over night before putting product back into it. 3/3/26- back on site this morning following up to make sure the 5 door cooler is still running properly. It is. Cooler running at set point and I graphed it on the E2 it ran fine all night. I told store they can put product back into it. Issue is resolved. Checked out with management. | Completed, summary attached Resource: Max Chesmore
|  |  | 2026-07-09 21:39 | Booking states 7/10 but no tech notes -Pinged Branch | Scheduled |  | WO-0611639 | Bolingbrook, IL | Dollar General #21257 | Kankakee | IL | Tavant/Product Care | STORE CONNECT | TEMPERATURE |  |  |  | RLN3MA / MY26F047544 |  | High Temperature Alarm
|  |  | 2026-07-08 21:05 | Drain Pain issue | Parts Needed |  | WO-0610829 | Dallas, TX | Dollar General #21778 | Kaufman | TX | 5177787 | FEXA | ICE BUILD UP |  |  |  | RLN3MA / MY26D028107 |  | There is a block of Ice on the inside at the top of unit | 7/10/26-Follow up. Case is dry and at temp this morning. Put into defrost to check drain. Still leaking. Believe interior portion of pan/drain line is cracked. Cannot be accessed without removing unit. Informed office of same. Someone will be out early next week to remove unit and take to shop for service. No new units in stock. Will see if office can order new drain pan assembly, as I'm not sure that it can be repaired. 7/10 - Right Side unit is problem side Per Trever, no new units to install. This unit will have to be repaired. Would try o get a new drain pan assembly if individual parts are available 7/9/26-PLEASE REFERENCE WO 0590766 FOR MORE PHOTOS AND INFORMATION. Case empty. Shut down and clean up all ice and water. Interior is completely dry now. Break away foam sealant to expose "drain line". Cannot tell if foam or foil tape was blocking drainage. Restart case. Will follow up in A.M. to make sure that drain functions, there may be other issues. I cannot check without allowing case to make water. Cannot access coil area to pour water into interior drain pan. More to follow. Case is back on, but store is not reloading until I am complete.
|  |  | 2026-07-08 19:55 | ETA 7/9 - No tech notes - Pinged branch | In Progress |  | WO-0610807 | Bolingbrook, IL | Dollar General #8773 | South Bend | IN | TAVANT/PRODUCT CARE | STORE CONNECT | TEMPERATURE |  |  |  | RLN3MA / MY26B016492 |  | High Temperature Alarm
|  |  | 2026-07-08 02:18 |  | Completed | 2026-07-10 | WO-0609997 | Southern | Dollar General #13009 | Wake Village | TX | TAVANT/PRODUCT CARE 5162403 | STORE CONNECT/FEXA | TEMPERATURE |  |  |  | RLN2MA / MY26C019875 |  | High Temperature Alarm / Invalid Temp reading +48 | Equipment: Tecumseh condensing unit Model: ALK440U-DS3B01 Serial: 04E0826121814 Work Performed: * Diagnosed system as being low on refrigerant. * Added R-290 refrigerant to restore the proper charge. * Sealed the system after charging. * Monitored operation and verified the unit returned to normal operation. * Box temperature pulled down to -5°F and was operating properly upon departure. * Verified refrigerant circuit and unit operation before leaving the site. Status: Unit running normally at -5°F at completion of
|  |  | 2026-07-14 13:55 |  | Unscheduled |  | WO-0614619 | Phoenix, AZ | Dollar General #10339 | Casa Grande | AZ | 5195296 | FEXA | LEAKING WATER |  |  |  | RLN3MA / MY26C025307 |  | Leaking into the freezer onto the product freezing it together
|  |  | 2026-07-13 16:59 |  | Completed | 2026-07-14 | WO-0614010 | Dallas, TX | Dollar General #10095 | Noonday | TX | TAVANT/PRODUCT CARE | STORE CONNECT | SENSOR |  |  |  | RMN3MA/MY26D026813 |  | Sensor Failure Alarm | 07/14/26; Check beer case, sn MY26D026813. E1 alarm, power cycle case controller, no change. Pull cover on the controller, found S1&S2 plug unpluged. Wiring extremely tight. Get slack in wiring and pluge back in. Restart unit, alarm cleared and unit came on. Temp dropping. E3 screen blank and won't come on, advise store mgr.
|  |  | 2026-07-13 16:33 | ETA 7/15 | Unscheduled |  | WO-0613989 | Houston, TX | Dollar General #12959 | Houston | TX | 5188500 | FEXA | COMPRESSOR |  |  |  | RLN2MA/MY26E034934 |  | Compressor is out making it smell like something is burning
|  |  | 2026-07-13 13:20 |  | Completed | 2026-07-13 | WO-0613796 | San Antonio, TX | Dollar General #20021 | San Antonio | TX | 5189787 | FEXA | DOOR ISSUE |  |  |  | RMN3MA / MY26C025322 |  | The Hinge on the top of door is broken . Can not open door all the way . | I got to store and check3d in with manager. I found door hold open not attached to door on middle door of 3 door case. I took a closer look and saw the door hold open was broken. I went to my truck and got a new door hold open. Took off the old one and installed the new one. I tested for proper operation. Checked out with manager.
|  |  | 2026-07-13 11:08 | ETA 7/14 | Scheduled |  | WO-0613652 | Gulf | Dollar General #22425 | Theodore | AL | 5183783 | FEXA | TEMPERATURE |  |  |  | RLN3MA / MY26F047552 |  | Unit not holding temp. Blinking HI
|  |  | 2026-07-13 03:31 |  | In Progress |  | WO-0613360 | Phoenix, AZ | Dollar General #21742 | Thoreau | NM | TAVANT/PRODUCT CARE | STORE CONNECT | TEMPERATURE |  |  |  | RLN3MA / MY26E034942 |  | High Temperature Alarm
|  |  | 2026-07-12 04:40 |  | Completed | 2026-07-12 | WO-0612961 | Houston, TX | Dollar General #12377 | Baytown | TX | TAVANT/PRODUCT CARE | STORE CONNECT | TEMPERATURE |  |  |  | RMN4MA / MY26D028118 |  | High Temperature Alarm | 7/12/26 I arrived and spoke with the manager. Located the case, was informed that the door on the case was left open last night, noted that all the doors would— stay open, tightened the torque rods on all four doors on the case, and now the doors on the case close automatically— after they are opened. Checked amp draw on the compressors, amp draw is good, checked fof ice on the evaporators, and there is no ice. Everything is working
|  |  | 2026-07-12 01:09 | NEED SUB/BRANCH to Run - Sent to Suzanne | Unscheduled |  | WO-0612947 |  | Dollar General #3359 | Littlefield | TX | TAVANT/PRODUCT CARE | STORE CONNECT | TEMPERATURE |  |  |  | RLN3MA / MY26B016010 |  | High Temperature Alarm
|  |  | 2026-07-11 21:37 |  | Completed | 2026-07-13 | WO-0612914 | Gulf | Dolalr General #22040 | Midland City | AL | TAVANT/PRODUCT CARE | STORE CONNECT | TEMPERATURE |  |  |  | RMN4MA / MY26F048133 |  | High Temperature Alarm | Found and repaired leak. Added 1 can r290 and confirmed operation and airflow
|  |  | 2026-07-11 21:12 |  | Completed | 2026-07-12 | WO-0612908 | Phoenix, AZ | Dollar General #21742 | Thoreau | NM | TAVANT/PRODUCT CARE | STORE CONNECT | TEMPERATURE |  |  |  | RLN3MA / MY26E034942 |  | High Temperature Alarm | 07/12/26 Robert Miller drive out to Thoreau arrived on site check in with store manager Audrey. She stated that all the Refrigeration equipment is running ok but there A/C has been down for three weeks store temperature was above 90°.We walk the cases found the Mod #RLN3MA Ser#MY26E034942 on workorder three glass doors frezzer. Temperature was at -05 troubleshoot per check list good airflow no ice build up on evap coils all fans are running. Check condenser unit the condenser coil was a little dirty clean coil put system in deforst check operation hot gas fans stop.Check operation of the three glass doors to make sure they was closing be of the store be so hot.All doors was operation closing good.Che k temperature drop down blow -02 after deforst. Check programming on the Carel controller all with spec. 07/11/26 Robert Miller got the call call the site talk with store manager Leona about Refrigeration cases.She stated that there was no alarms and the store would be closed before I get there not to come tonight morning service.
|  |  | 2026-07-11 19:14 |  | Completed | 2026-07-12 | WO-0612878 | Dallas, TX | Dollar General #21548 | Wills Point | TX | TIM SMITh | INTERNAL | TEMPERATURE | [5 empty] | Request Dallas Branch to repair RLNMA Low Temp Microblock not pulling to temp. We received confirmation a freezer that will not pull down to temp upon startup today. Model Serial TBD by technician. // This store is behind schedule and we are requesting priority service to repair asap. Suspect R290 units low on charge. // | Checked in and out withanager Amanda. Call was for new case running warm. At arrival the only case in alarm on the controller was the right microblock on the case i have attached data tag. This is a medium temperature case. Case is running 48°. Access microblock compressor. Suction line is not cold. Discharge lime is only warm. Shut power off to case. Leak checked. No leaks were found. No way to tell what pressure is on the system. Cut the sealed ends off of lone at compressor. Very little pressure came out. Added access fittings. Pulled vacuum. After vacuum i added 3.5 oz of R290 from truck stock. Turned unit on. Pressure was good and case dropped to temperature. Leak checked again now knowing the pressure of system. No leaks found. Case was likely shipped with correct charge. Attached pictures of all data tags found. Filled out refrigerant tracking. Added refrigerant from truck.stock to work order. Call complete.
|  |  | 2026-07-11 14:24 |  | Completed | 2026-07-11 | WO-0612734 | Southern | Dollar General #10520 | Youngsville | LA | TAVANT/PRODUCT CARE | STORE CONNECT | TEMPERATURE |  |  |  | RLN3MA / MY26E039362 |  | High Temperature Alarm | 07-11-2026 HUSSMANN MODEL ID: RLN3MA SERIAL- MY26E039362 COMPRESSOR MICROBLOCK MOD ALX440U-DS3B01 SER 04F0526122254 BM CRS0000675 Arrived on site and spoke with the manager. The manager showed me the freezer that was not cooling properly. The case temperature was 19°F and displaying a high-temperature alarm. Upon arrival, I immediately noticed that one of the freezer doors was being held open by a box of product lodged between the door and the door frame. I also observed that the right side of the freezer was overstocked, restricting proper airflow. I initiated several manual defrost cycles to clear any potential ice accumulation on the evaporator coils. While monitoring the unit, I also noticed extremely high ambient temperatures around the condenser section on top of the freezer. The condenser air intake temperature measured approximately 93°F. The compressors in the lineup were working continuously to reject heat, but the hot air was becoming trapped in the area, resulting in poor condenser performance and reduced subcooling. To improve heat rejection, I asked the store manager if a portable fan was available. The manager provided one, and the fan was store-used for this application. I positioned the fan on top of the lineup to move air across the condensers and exhaust the trapped heat. The improvement was immediate. Condenser temperatures dropped, subcooling increased, and the freezer temperature began pulling down into the negative range. The unit was operating normally upon departure. I also advised the manager to keep the freezer doors fully closed and avoid overstocking the case to maintain proper airflow and cooling performance.
|  |  | 2026-07-11 08:48 | NEED SUB/BRANCH to Run - Sent to Suzanne | Unscheduled |  | WO-0612539 |  | Dollar General #22086 | Oreana | IL | 5185715 | FEXA | TEMPERATURE |  |  |  | RLN3MA MY26E039361 |  | Invalid Temperature reading +61
|  |  | 2026-07-10 15:59 |  | Completed | 2026-07-13 | WO-0612255 | Southern | Dollar General #10520 | Youngsville | LA | 5185090 | FEXA | TEMPERATURE / BURNT SMELL |  |  |  | RLN3MA / MY26E039362 |  | Please look over cases and if needed recharge R290 Equipment. Freezer has a burnt/burning smell. Not holding temp, currently at 12 degrees | 7/13/26 Service call for microblock freezer high temp. Drove to site, checked in, gained access to freezer, freezer was in a defrost, no signs of burnt wiring, inspected case further, let defrost terminate, and case pulled down to temp., no issues were found. Case is opersting as it should as of now. Model: RLN3MA Serial: MY26E039362 Checked out with manager
|  |  | 2026-07-10 14:04 |  | Completed | 2026-07-13 | WO-0612151 | Houston, TX | Dollar General #12377 | Baytown | TX | TAVANT/PRODUCT CARE | STORE CONNECT | TEMPERATURE |  |  |  | RMN4MA / MY26F048132 |  | High Temperature Alarm | 7/13/2026 - Returned to Store case maintaining temperature no alarms present at this time 7/11/26 On arrival space temperature 85 degrees.ac units were offline another contractorworking on ac units.case temp 45 degrees.i did clean both condensers.high humidity in area.follow up work needed will return.
|  |  | 2026-07-10 10:02 | NEED SUB/BRANCH to Run - Sent to Suzanne | Unscheduled |  | WO-0611903 | RPM/Strategic Accounts | Dollar General #2606 | Logansport | IN | 5180847/PRODUCT CARE | STORE CONNECT/FEXA | DOOR ISSUE |  |  |  | RMN3MA / MY26E039395 |  | Door Hinge Does not work and Door stays open until manually shut
|  |  | 2026-07-20 |  | Completed | 2026-07-20 | WO-0618533 | Tulsa, OK | Dollar General #20336 | Ardmore | OK | TAVANT/PRODUCT CARE | STORE CONNECT | TEMPERATURE |  |  |  | RLN3MA / MY26B016487 |  | High Temperature Alarm | 7/20 Jake Hoppe found door frame heaters not working ice build up on the frame keeping doors open put evaps in defrost found wiring wrong not sending power to door frame wired up properly to get heat to frame removed iced and watched temp drop back down to setpoint and cycle
|  |  | 2026-07-19 |  | In Progress |  | WO-0618250 | Southern | Dollar General #4608 | Henderson | TX | 5211844 | FEXA | LEAKING WATER |  |  |  | RMN5MA / MY26E039407 |  | Beer Coole is leaking from the top inside of cooler causing cases of beer to fall apart. Cardboard of beer cases and 6 packs are wet
|  |  | 2026-07-18 12:15 | ETA 7/20 | Scheduled |  | WO-0617620 | Phoenix, AZ | Dollar General #22613 | Hereford | AZ | 5207369 | FEXA | LEAKING WATER |  |  |  | RLN3MA / MY26B016009 |  | There is water leaking from inside the unit from the top to the ceiling
|  |  | 2026-07-17 21:18 |  | Completed | 2026-07-19 | WO-0617378 | Southern | Dollar General #22247 | Ocean Springs | MS | TAVANT/PRODUCT CARE | STORE CONNECT | TEMPERATURE |  |  |  | RMN4MA / MY26F048122 |  | High Temperature Alarm | 7/19 Patrick Weems -Checked four door drink cooler model RMN4MA, Serial MY26F048122. Case at temp upon arrival. Checked all doors for proper closure. Found left side door staying open, door catching on top hinge socket mounting bolts. Removed door, tightened bolts. Reinstalled door, door now has proper clearance to close. Adjusted torque rod back. Door closing correctly, case at temp.
|  |  | 2026-07-17 06:33 |  | Completed | 2026-07-19 | WO-0616082 | Grand Rapids, MI | Dollar General #21404 | Andrews | IN | SUZANNE BASACA/PRODUCT CARE | INTERNAL/STORE CONNECT | TEMPERATURE |  |  |  | RMN3MA / MY26C025178 |  | Temperature | 7/19 Jake Berles Arrived on site checked in with manager. Brought in tools and supplies. Verified no refrigerant in system. Removed cracked line. Cut out bad section and reinstalled with tap. Pulled vacuum and recharge with 3.5oz of r290. Verified case pulled down to temp. Went over work performed and checked out.
|  |  | 2026-07-16 17:52 |  | Completed | 2026-07-17 | WO-0616509 | Dallas, TX | Dollar General #3277 | Garland | TX | 5201635 | FEXA | NOT WORKING AT ALL |  |  |  | RLN3MA / MY26d028108 MY26B015987 |  | Not working at all | 7/17 Christopher Boatner This case is at -8 the case next to it is the one that is down this is the wrong serial number case is full of product and frozen soild.
|  |  | 2026-07-15 21:43 |  | Completed | 2026-07-17 | WO-0615761 | Dallas, TX | Dollar General #3277 | Garland | TX | TAVANT/PRODUCT CARE | STORE CONNECT | TEMPERATURE |  |  |  | RLN3MA / MY26D028108 |  | High Temperature Alarm | 7/17 Christopher Boatner Upon arrival i found case in decrost water was coming out of bith boxes. I found center door with gasket pulled loosed and twisted around and causing air from store to go into case there is ice build up everywhere store is pulling i product and i will turn off case and return to start up . I retuned to store andcstarted up cases it took quite a while to pull down because case was 85 degrees. Also store air is not working in store its 80 degrees in the store so cases are struggling. Cases were at -8 when i left
|  |  | 2026-07-15 11:21 |  | Completed | 2026-07-15 | WO-0615276 | San Antonio, TX | Dollar General #20021 | San Antonio | TX | 5197464 | FEXA | LEAKING WATER |  |  |  | RMN4MA / MY26E038206 |  | Water is Leaking under unit | Upon arrival I checked in with store management and proceeded to the work being done. Walking up to the case i saw that there was water coming from under the case. I pulled the panel from underneath the case and inside the case. Underneath the case i saw the PVC drain line sweaty and causing condensation. I used co2 to blow out the drain and un clogged the drain. I tested the water pump and it is working. There was another company installing a drain pan with heater to the same unit. I cleared the drain line and system is working correctly at time. The inside of the case is dirty and chunks of slime is also part of why it is clogging up. I have attached all photos to the photo section of the WO
|  |  | 2026-07-14 15:30 | ETA 7/16 | Scheduled |  | WO-0614727 | Southern | Dollar General #13009 | Wake Village | TX | 5176386 | FEXA | TEMPERATURE |  |  |  | RLN2MA / MY26C019875 |  | Invalid Temperature Reading

## Settings
Root Cause Settings - dropdown source and clean-point rules | [10 empty] | Color sync note
Chart fills are static. If H/I hex values change, rerun the color sync to repaint charts.
Root Cause | Group | Owner | Status | Clean-Point Date | Clean Point 2 | Clean Point 3 | Clean-Point Serial | Display Order | Cause Color (hex) | Group Color (hex) |  | (grp first-seen) | Group List (auto)
Ref. leak/ Low charge | Ref. leak/ Low charge | Tecumseh | Closed | 2026-04-20 |  |  |  | 1 | 70AD47 | 70AD47 |  | 4 | Ref. leak/ Low charge
Door Torque | Doors | Hussmann MTY | Closed | 2026-06-05 | 2026-07-17 |  |  | 2 | FFC000 | FFC000 |  | 5 | Doors
Door Gasket | Doors | HSM MTY/RPM | Closed | 2026-06-05 | 2026-07-17 |  | NA | 3 | FFC000 | FFC000 |  |  | Drain tube blocked
Door frame heater | Doors | HSM MTY | Closed | 2026-06-05 | 2026-07-17 |  | NA | 4 | FFC000 | FFC000 |  |  | Wrong / Loose wiring
Door Torsion rod | Doors | HSM MTY/RPM | Closed | 2026-06-05 | 2026-07-17 |  | NA | 5 | FFC000 | FFC000 |  |  | Communication problem
Door not closed (Overnight) | Doors | HSM MTY/ RPM | Closed | 2026-06-05 | 2026-07-17 |  |  | 6 | FFC000 | FFC000 |  |  | High Store RH
Door - general | Doors | HSM | Closed | 2026-06-05 |  |  | NA | 7 | FFC000 | FFC000 |  |  | Enclosure Seal
Drain tube blocked | Drain tube blocked | Tecumseh | Closed | 2026-07-10 |  |  | 04G0926122771 | 8 | 4472C4 | 4472C4 |  | 11 | Component Failure
Wrong / Loose wiring | Wrong / Loose wiring | Tecumseh | Closed | 2026-03-27 |  |  |  | 9 | ED7D31 | ED7D31 |  | 12 | Defrost Sync
Communication problem | Communication problem | RPM | Open | 2026-06-18 |  |  | NA | 10 | 5B9BD5 | 5B9BD5 |  | 13 | False Alarm
High Store RH | High Store RH | DG | Closed | 2026-05-29 |  |  | NA | 11 | A5A5A5 | A5A5A5 |  | 14 | Setpoint change
Enclosure Seal | Enclosure Seal | Tecumseh | Closed | 2026-04-23 |  |  |  | 12 | 264478 | 264478 |  | 15 | Overstocking
Component Failure | Component Failure | Tecumseh | TBD | 2026-03-01 |  |  |  | 13 | 9E480E | 9E480E |  | 16 | Double defrost
Defrost Sync | Defrost Sync | HSM BGN | Closed | 2026-06-12 |  |  | NA | 14 | 636363 | 636363 |  | 17 | Return Air blocked
False Alarm | False Alarm | HSM BGN | Closed | 2026-05-22 |  |  | NA | 15 | 997300 | 997300 |  | 18 | Unidentified air leak
Setpoint change | Setpoint change | Tecumseh | Closed | 2026-03-16 |  |  |  | 16 | 255E93 | 255E93 |  | 19 | Freedom
Overstocking | Overstocking | DG | Closed | 2026-05-29 |  |  |  | 17 | 43682B | 43682B |  | 20 | Heavy case load
Double defrost | Double defrost | HSM MTY | Open | 2026-05-29 |  |  |  | 18 | 698ED0 | 698ED0 |  | 21 | Installation issue
Return Air blocked | Return Air blocked | DG | Closed | 2026-05-29 |  |  | NA | 19 | F1975A | F1975A |  | 22 | Unknown
Unidentified air leak | Unidentified air leak | HSM BGN | Open | 2026-06-16 |  |  | NA | 20 | B7B7B7 | B7B7B7 |  | 23 | Program change - Hussmann
Freedom | Freedom | NA | Closed | 2026-03-01 |  |  | NA | 21 | 1F4E79 | 1F4E79 |  | 24 | Wrong program
Heavy case load | Heavy case load | DG | Closed | 2026-05-29 |  |  | NA | 22 | C00000 | C00000 |  | 25
Installation issue | Installation issue | RPM | Open | 2026-05-29 |  |  | NA | 23 | 7030A0 | 7030A0 |  | 26
Unknown | Unknown | NA | Open | 2026-03-01 |  |  | NA | 24 | 2E75B6 | 2E75B6 |  | 27
Program change - Hussmann | Program change - Hussmann | HSM BGN | Open | 2026-05-29 |  |  | NA | 25 | BF9000 | BF9000 |  | 28
Wrong program | Wrong program | Tecumseh | Open |  |  |  | NA | 26 | 255E93 | 255E93 |  | 29
T-S2 Constants
Label | Value | Name
Max Summary rows | 240 | set_maxSummaryRow
Max Raw rows | 400 | set_maxRawRow
Max causes | 80 | set_maxCauses
Weeks shown | 20 | set_weeksShown
Tiebreak divisor | 100000 | set_tiebreakDivisor
T-S3 Serial prefixes
Prefix
RLN2MA
RLN3MA
RLN4MA
RMN4MA
RMN3MA
RMN5MA

## Store List
Store List - one row per store with commission date
DG Store # | Store Commission Date | City | State | Notes
Dollar General #13338 | 2026-03-11 | McRae | AR
Dollar General #20876 | 2026-03-31 | Elaine | AR
Dollar General #21375 | 2026-03-10 | Oxford | AR
Dollar General #22515 | 2026-03-09 | Fort Smith | AR
Dollar General #6827 | 2026-03-05 | Conway | AR
DOLLAR GENERAL #10369 | 2026-03-25 | Ajo | AZ
Dollar General #10339 | 2026-04-29 | Casa Grande | AZ
Dollar General #13396 | 2026-04-29 | Coolidge | AZ
Dollar General #13631 | 2026-05-05 | Quartzsite | AZ
Dollar General #14104 | 2026-03-24 | Tucson | AZ
Dollar General #16435 | 2026-03-25 | Tuba City | AZ
Dollar General #19997 | 2026-04-30 | Buckeye | AZ
Dollar General #22286 | 2026-03-18 | Arizona City | AZ
Dollar General #22613 | 2026-03-18 | Hereford | AZ
Dollar General #22864 | 2026-03-24 | Tucson | AZ
Dollar General #6987 | 2026-06-16 | Pinetop | AZ
Dollar General #21938 | 2026-07-01 | Olathe | CO
Dollar General #11509 | 2026-05-19 | Harvey | IL
Dollar General #14341 | 2026-04-20 | South Perkin | IL
Dollar General #14347 | 2026-04-22 | South Perkin | IL
Dollar General #20597 | 2026-04-22 | Chicago | IL
Dollar General #2600 | 2026-05-27 | Quincy | IL
Dollar General #20639 | 2026-04-13 | South Bend | IN
Dollar General #22281 | 2026-04-06 | Hamlet | IN
Dollar General #8773 | 2026-04-13 | South Bend | IN
Dollar General #10520 | 2026-06-26 | Youngsville | LA
Dollar General #20100 | 2026-06-17 | Paulina | LA
Dollar General #21838 | 2026-06-17 | Belle Chasse | LA
Dollar General #21415 | 2026-05-28 | Sulphur | LA
Dollar General #1247 | 2026-06-01 | Trenton | MO
Dollar General #14928 | 2026-05-12 | Nixa | MO
Dollar General #1768 | 2026-05-13 | Nixa | MO
Dollar General #21709 | 2026-05-27 | Eolia | MO
Dollar General # 13069 | 2026-04-15 | Laurel | MS
Dollar General # 13070 | 2026-04-14 | Laurel | MS
Dollar General #13069 | 2026-04-15 | Laurel | MS
Dollar General #21377 | 2026-03-12 | Starkville | MS
Dollar General #6372 | 2026-04-14 | Petal | MS
Dollar General #6099 | 2026-03-17 | Newton | NC
Dollar General #14386 | 2026-06-15 | Norman | OK
Dollar General #20336 | 2026-04-14 | Ardmore | OK
Dollar General #21606 | 2026-03-03 | Porum | OK
Dollar General #23988 | 2026-06-08 | Kingfisher | OK
Dollar General #21130 | 2026-04-13 | White City | OR
Dollar General #21342 | 2026-04-10 | Klamath Falls | OR
Dollar General #04117 | 2026-03-17 | Alvin | TX
Dollar General #12879 | 2026-03-25 | Dickinson | TX
Dollar General #13009 | 2026-05-27 | Wake Village | TX
Dollar General #14858 | 2026-03-16 | Houston | TX
Dollar General #20107 | 2026-05-06 | Baytown | TX
Dollar General #20407 | 2026-04-07 | Abilene | TX
Dollar General #20440 | 2026-05-19 | Sheridan | TX
Dollar General #20582 | 2026-03-17 | Houston | TX
Dollar General #20654 | 2026-03-25 | Alvin | TX
Dollar General #20761 | 2026-03-25 | Pettus | TX
Dollar General #21016 | 2026-04-07 | San Angelo | TX
Dollar General #21135 | 2026-03-25 | La Marque | TX
Dollar General #21223 | 2026-04-08 | Santa Anna | TX
Dollar General #21359 | 2026-04-28 | Orange | TX
Dollar General #21664 | 2026-06-30 | Jacksonville | TX
Dollar General #21778 | 2026-05-06 | Kaufman | TX
Dollar General #22149 | 2026-03-11 | Anton | TX
Dollar General #22408 | 2026-06-30 | Angelton | TX
Dollar General #22799 | 2026-03-18 | Amarillo | TX
Dollar General #22930 | 2026-04-16 | Forestburg | TX
Dollar General #22982 | 2026-04-14 | Ropesville | TX
Dollar General #3270 | 2026-04-08 | San Angelo | TX
Dollar General #3277 | 2026-05-07 | Garland | TX
Dollar General 22799 | 2026-03-18 | Amarillo | TX
Unknown legacy store | 2026-03-04
Dollar general #21257 | 2026-07-08 | Kankakee | IL
Dollar General #22187 | 2026-07-10 | Essex | IL
Dollar General 21548 | 2026-07-11 | Wills Point | TX
Dollar General #10095 | 2026-07-12 | Noonday | TX
Dollar General #20339 | 2026-07-09 | Porter | TX
Dollar General #05805 | 2026-07-09 | New Caney | TX
Dollar General #22040 | 2026-07-09 | Midland City | AL
Dollar General #21303 | 2026-07-07 | Rangely | CO
Dollar General #12959 | 2026-07-08 | Houston | TX
Dollar General #11114 | 2026-07-08 | Delta | UT
Dollar General #12377 | 2026-07-08 | Baytown | TX
Dollar General #2606 | 2026-07-06 | Logansport | IN
Dollar General #20981 | 2026-07-02 | Cortez | CO
Dollar General #04608 | 2026-06-30 | Henderson | TX
Dollar General #22523 | 2026-07-01 | Kilgore | TX
Dollar General #10864 | 2026-07-01 | Montrose | CO
Dollar General #22408 | 2026-06-30 | Angleton | TX
Dollar General #20375 | 2026-06-30 | Pearland | TX
Dollar General #22086 | 2026-06-22 | Oreana | IL
Dollar General #03397 | 2026-06-17 | San Antonio | TX
Dollar General #24075 | 2026-06-16 | Laplace | LA
Dollar General #10605 | 2026-06-17 | Show low | AZ
Dollar General #7408 | 2026-03-31 | Purcell | OK
Dollar General #21316 | 2026-03-04 | Tahlequah | OK
Dollar General #06827 | 2026-03-05 | Conway | AR
Dollar General #03359 | 2026-03-19 | Littlefield | TX
Dollar general #12449 | 2026-03-24 | Pasadena | TX
Dollar General #21300 | 2026-03-25 | Duncan | OK
Dollar general #8985 | 2026-03-23 | Mount Vernon | IL
Dollar General # 21409 | 2026-03-24 | Zeigler | IL
Dollar General #21072 | 2026-03-24 | Dahlgren | IL
Dollar General #09239 | 2026-03-18 | Conover | NC
Dollar General #06099 | 2026-03-17 | Newton | NC
Dollar General #21029 | 2026-03-09 | Lexa | AR
Dollar General #21541 | 2026-03-04 | Montevalo | AL
Dollar General #12870 | 2026-03-04 | Wooster | AR
Dollar General #22196 | 2026-03-04 | Brent | AL
Dollar General #00209 | 2026-01-08 | Augusta | AR
Dollar General #19907 | 2025-09-30 | Crossville | TN
Dollar General #22901 | 2026-04-27 | Norfolk | NE
Dollar General #22840 | 2026-04-16 | Lindsay | TX
Dollar General #21342 | 2026-04-14 | Klamath Falls | OR
Dollar General #8773 | 2026-04-13 | South Bend | IN
Dollar General #03270 | 2026-04-08 | San Angelo | TX
Dollar General #11624 | 2026-05-27 | amarillo | TX
Dollar General #31881 | 2026-05-27 | Bryans Road | MD
Dollar General #21590 | 2026-05-21 | Estancia | NM
Dollar General #21685 | 2026-05-21 | Cuba | NM
Dollar General #03637 | 2026-05-19 | Booneville | AR
Dollar general #22949 | 2026-05-18 | Wright City | OK
Dollar General #13064 | 2026-05-13 | Mobile | AL
Dollar General #07231 | 2026-05-13 | Springfield | MO
Dollar General #06987 | 2026-06-16 | Pinetop | AZ
Dollar General #21742 | 2026-06-16 | Thoreau | NM
Dollar General #02324 | 2026-06-10 | Norman | OK
Dollar General #20783 | 2026-06-10 | Del Rio | TX
Dollar General #14509 | 2026-06-11 | Mesa | AZ
Dollar General #22122 | 2026-06-09 | Velva | ND
Dollar General #20021 | 2026-06-10 | San Antonio | TX
Dollar General #10215 | 2026-06-09 | Show Low | AZ
Dollar General #11365 | 2026-05-07 | Pine Bluff | AR
Dollar General #22925 | 2026-06-08 | Black Hawk | SD
Dollar General #22074 | 2026-05-21 | Lockhart | TX
Dollar General #23202 | 2026-06-03 | Colfax | LA
Dollar General #13548 | 2026-05-20 | Charlotte | NC
Dollar General #21274 | 2026-06-02 | Dequincy | LA
Dollar General #20721 | 2026-06-01 | Harrisville | MI
Dollar General #06996 | 2026-05-06 | Baytown | TX
Dollar General #21322 | 2026-03-31 | Hickory | KY
Dollar General #03277 | 2026-05-07 | Garland | TX
Dollar General #01768 | 2026-05-13 | Nixa | MO
Dollar General #21589 | 2026-03-26 | Vidalia | LA
Dollar General #21070 | 2026-03-31 | Cisne | IL
Dollar General #22334 | 2026-05-28 | Lake Charles | LA
Dollar General #20732 | 2026-05-27 | Bloomburg | TX
Dollar General #07285 | 2026-05-27 | Amarillo | TX
Dollar General #22419 | 2026-05-05 | Beaumont | TX
Dollar General #21516 | 2026-05-26 | Anderson | TX
Dollar General #00731 | 2026-05-05 | Searcy | AR
Dollar General #02600 | 2026-05-27 | Quincy | IL
Dollar General #31839 | 2026-05-13 | Jacksonville | AL
Dollar General #13953 |  | Allen | OK
Dollar General #06559 |  | Gardendale | AL
Dollar General #06314 |  | Northport | AL
Dollar General #06550 | 2026-05-05 | Jacinto | TX
Dollar General #13693 |  | Maryland Heights | MO
Dollar General #21829 |  | Hazelwood | MO
Dollar General #24159 |  | Herculaneum | MO
Dollar General #21783 |  | East Bethel | MN
Dollar General #00279 |  | Fouke | AR
Dollar General #22107 | 2026-05-18 | Waubun | MN
Dollar General #09806 | 2024-09-18 | Scottsville | KY
Dollar General #25692 |  | Charlotte | NC
Dollar General #08790 |  | Lafayette | LA
Dollar General #30977 | 2024-08-27 | Scottsboro | AL
Dollar General #10884 | 2024-08-20 | Cullman | AL
Dollar General #03217 | 2024-07-29 | Lillington | NC
Dollar General #02332 | 2024-08-27 | Sylacauga | AL
Dollar General #03000 |  | Florissant | MO
Dollar General #06026 |  | Overland | MO
Dollar General #4608 | 2026-06-30 | Henderson | TX
Dollar General #22247 | 2026-07-16 | Ocean Springs | MS
Dollar General #21404 | 2026-07-15 | Andrews | IN

## Calc_Weekly (hidden)
T-W1/T-W2/T-W3 Weekly pivots
Three stacked pivots: commission week by root cause, call week by root cause, and commission week by group. Week rows remain capped by Settings!Weeks shown.
Commission week by root cause
| Group | Ref. leak/ Low charge | Doors | Doors | Doors | Doors | Doors | Doors | Drain tube blocked | Wrong / Loose wiring | Communication problem | High Store RH | Enclosure Seal | Component Failure | Defrost Sync | False Alarm | Setpoint change | Overstocking | Double defrost | Return Air blocked | Unidentified air leak | Freedom | Heavy case load | Installation issue | Unknown | Program change - Hussmann | Wrong program | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Week Start | Root Cause | Ref. leak/ Low charge | Door Torque | Door Gasket | Door frame heater | Door Torsion rod | Door not closed (Overnight) | Door - general | Drain tube blocked | Wrong / Loose wiring | Communication problem | High Store RH | Enclosure Seal | Component Failure | Defrost Sync | False Alarm | Setpoint change | Overstocking | Double defrost | Return Air blocked | Unidentified air leak | Freedom | Heavy case load | Installation issue | Unknown | Program change - Hussmann | Wrong program | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-03-02 | Mar 2 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-03-09 | Mar 9 | 0 | 1 | 0 | 0 | 0 | 2 | 1 | 1 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-03-16 | Mar 16 | 3 | 3 | 0 | 1 | 0 | 1 | 1 | 1 | 2 | 4 | 0 | 2 | 0 | 1 | 2 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-03-23 | Mar 23 | 0 | 3 | 2 | 0 | 0 | 1 | 0 | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-03-30 | Mar 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-04-06 | Apr 6 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 1 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-04-13 | Apr 13 | 1 | 1 | 0 | 1 | 0 | 2 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-04-20 | Apr 20 | 0 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-04-27 | Apr 27 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-04 | May 4 | 0 | 1 | 1 | 0 | 0 | 2 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-11 | May 11 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-18 | May 18 | 0 | 1 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-25 | May 25 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-06-01 | Jun 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-06-08 | Jun 8 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-06-15 | Jun 15 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 2 | 0 | 1 | 0 | 2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-06-22 | Jun 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-06-29 | Jun 29 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-07-06 | Jul 6 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-07-13 | Jul 13 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-07-20 | Jul 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-07-27 | Jul 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-08-03 | Aug 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-08-10 | Aug 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-08-17 | Aug 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-08-24 | Aug 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-08-31 | Aug 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-09-07 | Sep 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-09-14 | Sep 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-09-21 | Sep 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-09-28 | Sep 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-10-05 | Oct 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-10-12 | Oct 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-10-19 | Oct 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-10-26 | Oct 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-11-02 | Nov 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-11-09 | Nov 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-11-16 | Nov 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-11-23 | Nov 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-11-30 | Nov 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-12-07 | Dec 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-12-14 | Dec 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-12-21 | Dec 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-12-28 | Dec 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2027-01-04 | Jan 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total |  | 11 | 13 | 5 | 5 | 1 | 13 | 7 | 12 | 7 | 10 | 12 | 3 | 6 | 4 | 15 | 1 | 4 | 1 | 1 | 2 | 5 | 1 | 8 | 7 | 1 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Commission week by root cause - after clean point
| Group | Ref. leak/ Low charge | Doors | Doors | Doors | Doors | Doors | Doors | Drain tube blocked | Wrong / Loose wiring | Communication problem | High Store RH | Enclosure Seal | Component Failure | Defrost Sync | False Alarm | Setpoint change | Overstocking | Double defrost | Return Air blocked | Unidentified air leak | Freedom | Heavy case load | Installation issue | Unknown | Program change - Hussmann | Wrong program | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Week Start | Root Cause | Ref. leak/ Low charge | Door Torque | Door Gasket | Door frame heater | Door Torsion rod | Door not closed (Overnight) | Door - general | Drain tube blocked | Wrong / Loose wiring | Communication problem | High Store RH | Enclosure Seal | Component Failure | Defrost Sync | False Alarm | Setpoint change | Overstocking | Double defrost | Return Air blocked | Unidentified air leak | Freedom | Heavy case load | Installation issue | Unknown | Program change - Hussmann | Wrong program | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-03-02 | Mar 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-03-09 | Mar 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-03-16 | Mar 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-03-23 | Mar 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-03-30 | Mar 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-04-06 | Apr 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-04-13 | Apr 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-04-20 | Apr 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-04-27 | Apr 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-04 | May 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-11 | May 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-18 | May 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-25 | May 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-06-01 | Jun 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-06-08 | Jun 8 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-06-15 | Jun 15 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 2 | 0 | 1 | 0 | 2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-06-22 | Jun 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-06-29 | Jun 29 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-07-06 | Jul 6 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-07-13 | Jul 13 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-07-20 | Jul 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-07-27 | Jul 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-08-03 | Aug 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-08-10 | Aug 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-08-17 | Aug 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-08-24 | Aug 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-08-31 | Aug 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-09-07 | Sep 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-09-14 | Sep 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-09-21 | Sep 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-09-28 | Sep 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-10-05 | Oct 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-10-12 | Oct 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-10-19 | Oct 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-10-26 | Oct 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-11-02 | Nov 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-11-09 | Nov 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-11-16 | Nov 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-11-23 | Nov 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-11-30 | Nov 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-12-07 | Dec 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-12-14 | Dec 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-12-21 | Dec 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-12-28 | Dec 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2027-01-04 | Jan 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total |  | 2 | 1 | 0 | 0 | 1 | 2 | 2 | 0 | 2 | 1 | 4 | 0 | 6 | 0 | 5 | 1 | 3 | 0 | 0 | 0 | 5 | 0 | 2 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Call week by root cause
| Group | Ref. leak/ Low charge | Doors | Doors | Doors | Doors | Doors | Doors | Drain tube blocked | Wrong / Loose wiring | Communication problem | High Store RH | Enclosure Seal | Component Failure | Defrost Sync | False Alarm | Setpoint change | Overstocking | Double defrost | Return Air blocked | Unidentified air leak | Freedom | Heavy case load | Installation issue | Unknown | Program change - Hussmann | Wrong program | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Week Start | Root Cause | Ref. leak/ Low charge | Door Torque | Door Gasket | Door frame heater | Door Torsion rod | Door not closed (Overnight) | Door - general | Drain tube blocked | Wrong / Loose wiring | Communication problem | High Store RH | Enclosure Seal | Component Failure | Defrost Sync | False Alarm | Setpoint change | Overstocking | Double defrost | Return Air blocked | Unidentified air leak | Freedom | Heavy case load | Installation issue | Unknown | Program change - Hussmann | Wrong program | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-03-09 08:16 | Mar 9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-03-16 08:16 | Mar 16 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-03-23 08:16 | Mar 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-03-30 08:16 | Mar 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-04-06 08:16 | Apr 6 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 2 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-04-13 08:16 | Apr 13 | 2 | 1 | 0 | 0 | 0 | 0 | 3 | 1 | 1 | 0 | 1 | 0 | 0 | 2 | 2 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-04-20 08:16 | Apr 20 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-04-27 08:16 | Apr 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-04 08:16 | May 4 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-11 08:16 | May 11 | 3 | 0 | 0 | 1 | 0 | 0 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-18 08:16 | May 18 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-25 08:16 | May 25 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-06-01 08:16 | Jun 1 | 2 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-06-08 08:16 | Jun 8 | 0 | 2 | 2 | 1 | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-06-15 08:16 | Jun 15 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-06-22 08:16 | Jun 22 | 0 | 2 | 1 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-06-29 08:16 | Jun 29 | 0 | 0 | 0 | 1 | 1 | 3 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-07-06 08:16 | Jul 6 | 2 | 3 | 0 | 0 | 0 | 2 | 0 | 2 | 0 | 0 | 5 | 0 | 0 | 0 | 1 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-07-13 08:16 | Jul 13 | 0 | 0 | 2 | 1 | 0 | 0 | 2 | 2 | 0 | 1 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-07-20 08:16 | Jul 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-07-27 08:16 | Jul 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-08-03 08:16 | Aug 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-08-10 08:16 | Aug 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-08-17 08:16 | Aug 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-08-24 08:16 | Aug 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-08-31 08:16 | Aug 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-09-07 08:16 | Sep 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-09-14 08:16 | Sep 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-09-21 08:16 | Sep 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-09-28 08:16 | Sep 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-10-05 08:16 | Oct 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-10-12 08:16 | Oct 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-10-19 08:16 | Oct 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-10-26 08:16 | Oct 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-11-02 08:16 | Nov 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-11-09 08:16 | Nov 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-11-16 08:16 | Nov 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-11-23 08:16 | Nov 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-11-30 08:16 | Nov 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-12-07 08:16 | Dec 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-12-14 08:16 | Dec 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-12-21 08:16 | Dec 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-12-28 08:16 | Dec 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2027-01-04 08:16 | Jan 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2027-01-11 08:16 | Jan 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total |  | 13 | 13 | 5 | 5 | 1 | 13 | 7 | 12 | 7 | 10 | 13 | 3 | 6 | 4 | 16 | 1 | 4 | 1 | 1 | 2 | 6 | 1 | 9 | 7 | 1 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Commission week by group
Week Start | Week Label | Ref. leak/ Low charge | Doors | Drain tube blocked | Wrong / Loose wiring | Communication problem | High Store RH | Enclosure Seal | Component Failure | Defrost Sync | False Alarm | Setpoint change | Overstocking | Double defrost | Return Air blocked | Unidentified air leak | Freedom | Heavy case load | Installation issue | Unknown | Program change - Hussmann | Wrong program
2026-03-02 | Mar 2 | 0 | 2 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-03-09 | Mar 9 | 0 | 4 | 1 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2026-03-16 | Mar 16 | 3 | 6 | 1 | 2 | 4 | 0 | 2 | 0 | 1 | 2 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 1
2026-03-23 | Mar 23 | 0 | 6 | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2026-03-30 | Mar 30 | 0 | 0 | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-04-06 | Apr 6 | 5 | 0 | 0 | 0 | 2 | 0 | 0 | 1 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2 | 0 | 0
2026-04-13 | Apr 13 | 1 | 5 | 1 | 0 | 0 | 1 | 1 | 1 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 3 | 0 | 0
2026-04-20 | Apr 20 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
2026-04-27 | Apr 27 | 0 | 2 | 1 | 0 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-04 | May 4 | 0 | 4 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
2026-05-11 | May 11 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-05-18 | May 18 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0
2026-05-25 | May 25 | 0 | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
2026-06-01 | Jun 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-06-08 | Jun 8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
2026-06-15 | Jun 15 | 0 | 2 | 0 | 0 | 0 | 2 | 0 | 1 | 0 | 2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-06-22 | Jun 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-06-29 | Jun 29 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
2026-07-06 | Jul 6 | 0 | 1 | 1 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1
2026-07-13 | Jul 13 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
2026-07-20 | Jul 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-07-27 | Jul 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-08-03 | Aug 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-08-10 | Aug 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-08-17 | Aug 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-08-24 | Aug 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-08-31 | Aug 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-09-07 | Sep 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-09-14 | Sep 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-09-21 | Sep 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-09-28 | Sep 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-10-05 | Oct 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-10-12 | Oct 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-10-19 | Oct 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-10-26 | Oct 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-11-02 | Nov 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-11-09 | Nov 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-11-16 | Nov 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-11-23 | Nov 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-11-30 | Nov 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-12-07 | Dec 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-12-14 | Dec 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-12-21 | Dec 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026-12-28 | Dec 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2027-01-04 | Jan 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total |  | 11 | 44 | 12 | 7 | 10 | 12 | 3 | 6 | 4 | 15 | 1 | 4 | 1 | 1 | 2 | 5 | 1 | 8 | 7 | 1 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Calc_Charts (hidden)
Calc_Charts
T1. Cause totals (filtered)
Mirrors Graphs K:N; filtered cause counts and after-clean counts; feeds group/rank calculations. | [22 empty] | Ref. leak/ Low charge | Ref. leak/ Low charge | 4 | 2 | 4
Root Cause | Total in window | After clean point | Tiebreak | [19 empty] | Door Torque | Doors | 7 | 1 | 5
Ref. leak/ Low charge | 4 | 2 | 4.0004 | [19 empty] | Door Gasket | Doors | 5 | 0
Door Torque | 7 | 1 | 7.0004 | [19 empty] | Door frame heater | Doors | 4 | 0
Door Gasket | 5 | 0 | 5.0004 | [19 empty] | Door Torsion rod | Doors | 1 | 1
Door frame heater | 4 | 0 | 4.0004 | [19 empty] | Door not closed (Overnight) | Doors | 13 | 2
Door Torsion rod | 1 | 1 | 1.0004 | [19 empty] | Door - general | Doors | 2 | 2
Door not closed (Overnight) | 13 | 2 | 13.0003 | [19 empty] | Drain tube blocked | Drain tube blocked | 5 | 0 | 11
Door - general | 2 | 2 | 2.0003 | [19 empty] | Wrong / Loose wiring | Wrong / Loose wiring | 2 | 2 | 12
Drain tube blocked | 5 | 0 | 5.0003 | [19 empty] | Communication problem | Communication problem | 5 | 1 | 13
Wrong / Loose wiring | 2 | 2 | 2.0003 | [19 empty] | High Store RH | High Store RH | 9 | 4 | 14
Communication problem | 5 | 1 | 5.0003 | [19 empty] | Enclosure Seal | Enclosure Seal | 0 | 0 | 15
High Store RH | 9 | 4 | 9.0003 | [19 empty] | Component Failure | Component Failure | 2 | 2 | 16
Enclosure Seal | 0 | 0 | 0.00029 | [19 empty] | Defrost Sync | Defrost Sync | 0 | 0 | 17
Component Failure | 2 | 2 | 2.0003 | [19 empty] | False Alarm | False Alarm | 12 | 5 | 18
Defrost Sync | 0 | 0 | 0.00027 | [19 empty] | Setpoint change | Setpoint change | 1 | 1 | 19
False Alarm | 12 | 5 | 12.0003 | [19 empty] | Overstocking | Overstocking | 3 | 3 | 20
Setpoint change | 1 | 1 | 1.0003 | [19 empty] | Double defrost | Double defrost | 0 | 0 | 21
Overstocking | 3 | 3 | 3.0002 | [19 empty] | Return Air blocked | Return Air blocked | 0 | 0 | 22
Double defrost | 0 | 0 | 0.00023 | [19 empty] | Unidentified air leak | Unidentified air leak | 0 | 0 | 23
Return Air blocked | 0 | 0 | 0.00022 | [19 empty] | Freedom | Freedom | 2 | 2 | 24
Unidentified air leak | 0 | 0 | 0.00021 | [19 empty] | Heavy case load | Heavy case load | 0 | 0 | 25
Freedom | 2 | 2 | 2.0002 | [19 empty] | Installation issue | Installation issue | 6 | 2 | 26
Heavy case load | 0 | 0 | 0.00019 | [19 empty] | Unknown | Unknown | 5 | 5 | 27
Installation issue | 6 | 2 | 6.0002 | [19 empty] | Program change - Hussmann | Program change - Hussmann | 0 | 0 | 28
Unknown | 5 | 5 | 5.0002 | [19 empty] | Wrong program | Wrong program | 1 | 0 | 29
Program change - Hussmann | 0 | 0 | 0.00016 | [19 empty] | 0 | 0 | 0 | 0 | 30
[23 empty] | 0 | 0 | 0 | 0
[23 empty] | 0 | 0 | 0 | 0
T2. Group totals (filtered) | [22 empty] | 0 | 0 | 0 | 0
Mirrors Graphs P:U plus dedup helper; unique groups, totals, after-clean totals, and sort helpers. | [22 empty] | 0 | 0 | 0 | 0
Group | First-occurrence row | Total | After clean | Total tiebreak | After tiebreak | [17 empty] | 0 | 0 | 0 | 0
Ref. leak/ Low charge | 4 | 4 | 2 | 4.0003 | 2.0002 | [17 empty] | 0 | 0 | 0 | 0
Doors | 5 | 32 | 6 | 32.0002 | 6.0002 | [17 empty] | 0 | 0 | 0 | 0
Drain tube blocked | 11 | 5 | 0 | 5.0002 | 0.00023 | [17 empty] | 0 | 0 | 0 | 0
Wrong / Loose wiring | 12 | 2 | 2 | 2.0002 | 2.0002 | [17 empty] | 0 | 0 | 0 | 0
Communication problem | 13 | 5 | 1 | 5.0002 | 1.0002 | [17 empty] | 0 | 0 | 0 | 0
High Store RH | 14 | 9 | 4 | 9.0002 | 4.0002 | [17 empty] | 0 | 0 | 0 | 0
Enclosure Seal | 15 | 0 | 0 | 0.00019 | 0.00019 | [17 empty] | 0 | 0 | 0 | 0
Component Failure | 16 | 2 | 2 | 2.0002 | 2.0002 | [17 empty] | 0 | 0 | 0 | 0
Defrost Sync | 17 | 0 | 0 | 0.00017 | 0.00017 | [17 empty] | 0 | 0 | 0 | 0
False Alarm | 18 | 12 | 5 | 12.0002 | 5.0002 | [17 empty] | 0 | 0 | 0 | 0
Setpoint change | 19 | 1 | 1 | 1.0002 | 1.0002 | [17 empty] | 0 | 0 | 0 | 0
Overstocking | 20 | 3 | 3 | 3.0001 | 3.0001 | [17 empty] | 0 | 0 | 0 | 0
Double defrost | 21 | 0 | 0 | 0.00013 | 0.00013 | [17 empty] | 0 | 0 | 0 | 0
Return Air blocked | 22 | 0 | 0 | 0.00012 | 0.00012 | [17 empty] | 0 | 0 | 0 | 0
Unidentified air leak | 23 | 0 | 0 | 0.00011 | 0.00011 | [17 empty] | 0 | 0 | 0 | 0
Freedom | 24 | 2 | 2 | 2.0001 | 2.0001 | [17 empty] | 0 | 0 | 0 | 0
Heavy case load | 25 | 0 | 0 | 9e-05 | 9e-05 | [17 empty] | 0 | 0 | 0 | 0
Installation issue | 26 | 6 | 2 | 6.0001 | 2.0001 | [17 empty] | 0 | 0 | 0 | 0
Unknown | 27 | 5 | 5 | 5.0001 | 5.0001 | [17 empty] | 0 | 0 | 0 | 0
Program change - Hussmann | 28 | 0 | 0 | 6e-05 | 6e-05 | [17 empty] | 0 | 0 | 0 | 0
Wrong program | 29 | 1 | 0 | 1.0001 | 5e-05 | [17 empty] | 0 | 0 | 0 | 0
|  |  |  | 4e-05 | 4e-05 | [17 empty] | 0 | 0 | 0 | 0
|  |  |  | 3e-05 | 3e-05 | [17 empty] | 0 | 0 | 0 | 0
|  |  |  | 2e-05 | 2e-05 | [17 empty] | 0 | 0 | 0 | 0
|  |  |  | 1e-05 | 1e-05
T3. Ranked by total
Mirrors Graphs V:W; sorted desc with zero-bar hiding through ch1_cats/ch1_vals.
Ranked group | Total | Ref. leak/ Low charge | Doors | Drain tube blocked | Wrong / Loose wiring | Communication problem | High Store RH | Enclosure Seal | Component Failure | Defrost Sync | False Alarm | Setpoint change | Overstocking | Double defrost | Return Air blocked | Unidentified air leak | Freedom | Heavy case load | Installation issue | Unknown | Program change - Hussmann | Wrong program
Doors | 32 |  | 32
False Alarm | 12 | [9 empty] | 12
High Store RH | 9 | [5 empty] | 9
Installation issue | 6 | [17 empty] | 6
Drain tube blocked | 5 |  |  | 5
Communication problem | 5 |  |  |  |  | 5
Unknown | 5 | [18 empty] | 5
Ref. leak/ Low charge | 4 | 4
Overstocking | 3 | [11 empty] | 3
Wrong / Loose wiring | 2 |  |  |  | 2
Component Failure | 2 | [7 empty] | 2
Freedom | 2 | [15 empty] | 2
Setpoint change | 1 | [10 empty] | 1
Wrong program | 1 | [20 empty] | 1
Enclosure Seal | 0
Defrost Sync | 0
Double defrost | 0
Return Air blocked | 0
Unidentified air leak | 0
Heavy case load | 0
Program change - Hussmann | 0
Value | 0
240 | 0
400 | 0
80 | 0
T4. Ranked by after-clean
Mirrors Graphs X:Y; sorted desc with zero-bar hiding through ch3_cats/ch3_vals.
Ranked group | After clean | Ref. leak/ Low charge | Doors | Drain tube blocked | Wrong / Loose wiring | Communication problem | High Store RH | Enclosure Seal | Component Failure | Defrost Sync | False Alarm | Setpoint change | Overstocking | Double defrost | Return Air blocked | Unidentified air leak | Freedom | Heavy case load | Installation issue | Unknown | Program change - Hussmann | Wrong program
Doors | 6 |  | 6
False Alarm | 5 | [9 empty] | 5
Unknown | 5 | [18 empty] | 5
High Store RH | 4 | [5 empty] | 4
Overstocking | 3 | [11 empty] | 3
Ref. leak/ Low charge | 2 | 2
Wrong / Loose wiring | 2 |  |  |  | 2
Component Failure | 2 | [7 empty] | 2
Freedom | 2 | [15 empty] | 2
Installation issue | 2 | [17 empty] | 2
Communication problem | 1 |  |  |  |  | 1
Setpoint change | 1 | [10 empty] | 1
Drain tube blocked | 0
Enclosure Seal | 0
Defrost Sync | 0
Double defrost | 0
Return Air blocked | 0
Unidentified air leak | 0
Heavy case load | 0
Program change - Hussmann | 0
Wrong program | 0
Value | 0
240 | 0
400 | 0
80 | 0
T5. Chart-5 stack feed
Mirrors Graphs DD:DG; ranked group, after, before, and total; feeds c5 categories and labels.
Ranked group | After | Before | Total
Doors | 6 | 26 | 32
False Alarm | 5 | 7 | 12
High Store RH | 4 | 5 | 9
Installation issue | 2 | 4 | 6
Drain tube blocked | 0 | 5 | 5
Communication problem | 1 | 4 | 5
Unknown | 5 | 0 | 5
Ref. leak/ Low charge | 2 | 2 | 4
Overstocking | 3 | 0 | 3
Wrong / Loose wiring | 2 | 0 | 2
Component Failure | 2 | 0 | 2
Freedom | 2 | 0 | 2
Setpoint change | 1 | 0 | 1
Wrong program | 0 | 1 | 1
Enclosure Seal | 0 | 0 | 0
Defrost Sync | 0 | 0 | 0
Double defrost | 0 | 0 | 0
Return Air blocked | 0 | 0 | 0
Unidentified air leak | 0 | 0 | 0
Heavy case load | 0 | 0 | 0
Program change - Hussmann | 0 | 0 | 0
Value | 0 | 0 | 0
240 | 0 | 0 | 0
400 | 0 | 0 | 0
80 | 0 | 0 | 0
T6. Chart-5 diagonal matrix
Series n = After value only at rank n; fixed bar-rank colors while labels follow ranking; feeds ch5_seg01...ch5_seg25.
Ranked group | Ref. leak/ Low charge | Doors | Drain tube blocked | Wrong / Loose wiring | Communication problem | High Store RH | Enclosure Seal | Component Failure | Defrost Sync | False Alarm | Setpoint change | Overstocking | Double defrost | Return Air blocked | Unidentified air leak | Freedom | Heavy case load | Installation issue | Unknown | Program change - Hussmann | Wrong program
Doors |  | 6
False Alarm | [9 empty] | 5
High Store RH | [5 empty] | 4
Installation issue | [17 empty] | 2
Drain tube blocked
Communication problem |  |  |  |  | 1
Unknown | [18 empty] | 5
Ref. leak/ Low charge | 2
Overstocking | [11 empty] | 3
Wrong / Loose wiring |  |  |  | 2
Component Failure | [7 empty] | 2
Freedom | [15 empty] | 2
Setpoint change | [10 empty] | 1
Wrong program
Enclosure Seal
Defrost Sync
Double defrost
Return Air blocked
Unidentified air leak
Heavy case load
Program change - Hussmann
Value
240
400
80
T7. Week labels + totals for charts 2 & 4
Labels derive from Calc_Weekly week-start dates; replaces hardcoded Graphs AN:AO labels and feeds total label series.
Commission label | Commission total | Call label | Call total
03/02 | 6 | 03/09 | 4
03/09 | 7 | 03/16 | 3
03/16 | 25 | 03/23 | 2
03/23 | 16 | 03/30 | 4
03/30 | 4 | 04/06 | 9
04/06 | 15 | 04/13 | 16
04/13 | 17 | 04/20 | 8
04/20 | 6 | 04/27 | 1
04/27 | 7 | 05/04 | 5
05/04 | 10 | 05/11 | 11
05/11 | 2 | 05/18 | 4
05/18 | 5 | 05/25 | 6
05/25 | 6 | 06/01 | 8
06/01 | 2 | 06/08 | 15
06/08 | 3 | 06/15 | 8
06/15 | 8 | 06/22 | 13
06/22 | 4 | 06/29 | 12
06/29 | 5 | 07/06 | 18
07/06 | 5 | 07/13 | 14
07/13 | 2 | 07/20 | 0
T8. Group rollup (from old Counts)
Mirrors Counts group rollup; total, visible, and after-clean lines by group.
Group | Total Lines | Visible Lines | After Clean Point
Ref. leak/ Low charge | 13 | 0 | 2
Doors | 44 | 0 | 6
Drain tube blocked | 12 | 0 | 0
Wrong / Loose wiring | 7 | 0 | 2
Communication problem | 10 | 0 | 1
High Store RH | 13 | 1 | 4
Enclosure Seal | 3 | 0 | 0
Component Failure | 6 | 0 | 6
Defrost Sync | 4 | 0 | 0
False Alarm | 16 | 0 | 5
Setpoint change | 1 | 0 | 1
Overstocking | 4 | 0 | 3
Double defrost | 1 | 0 | 0
Return Air blocked | 1 | 0 | 0
Unidentified air leak | 2 | 0 | 0
Freedom | 6 | 0 | 5
Heavy case load | 1 | 0 | 0
Installation issue | 9 | 0 | 2
Unknown | 7 | 0 | 7
Program change - Hussmann | 1 | 0 | 0
Wrong program | 4 | 0 | 0
Value | 0 | 0 | 0
240 | 0 | 0 | 0
400 | 0 | 0 | 0
80 | 0 | 0 | 0
T9. Case nomenclature counts
Uses Settings serial prefixes and SEARCH-based count formulas; feeds Chart 6.
Serial prefix | Count
RLN2MA | 22
RLN3MA | 36
RLN4MA | 3
RMN4MA | 15
RMN3MA | 7
RMN5MA | 5
T10. Chart titles
Dynamic title formulas linked to chart title StrRefs.
Chart | Title
Chart 1 | Issues by root cause (Jun 1 to Jul 22)
Chart 2 | Dispatch by store commission week (by cause group)
Chart 3 | Issues after clean point (Jun 1 to Jul 22)
Chart 4 | Dispatch by call week (by root cause)
Chart 5 | Issues by root cause - after vs before clean point (Jun 1 to Jul 22)
Chart 6 | Issues by case nomenclature (Jun 1 to Jul 22)
Jun 1 to Jul 22
T11. RLN3MA - after vs before by group
Prefix from cell below; filters Summary by serial prefix + timeline; feeds Chart 7 via ch*.
Nomenclature: | RLN3MA
Root Cause | Group | Total | After
Ref. leak/ Low charge | Ref. leak/ Low charge | 0 | 0
Door Torque | Doors | 2 | 0
Door Gasket | Doors | 3 | 0
Door frame heater | Doors | 4 | 0
Door Torsion rod | Doors | 0 | 0
Door not closed (Overnight) | Doors | 5 | 1
Door - general | Doors | 0 | 0
Drain tube blocked | Drain tube blocked | 3 | 0
Wrong / Loose wiring | Wrong / Loose wiring | 2 | 2
Communication problem | Communication problem | 0 | 0
High Store RH | High Store RH | 5 | 2
Enclosure Seal | Enclosure Seal | 0 | 0
Component Failure | Component Failure | 0 | 0
Defrost Sync | Defrost Sync | 0 | 0
False Alarm | False Alarm | 5 | 2
Setpoint change | Setpoint change | 0 | 0
Overstocking | Overstocking | 2 | 2
Double defrost | Double defrost | 0 | 0
Return Air blocked | Return Air blocked | 0 | 0
Unidentified air leak | Unidentified air leak | 0 | 0
Freedom | Freedom | 0 | 0
Heavy case load | Heavy case load | 0 | 0
Installation issue | Installation issue | 2 | 0
Unknown | Unknown | 2 | 2
Program change - Hussmann | Program change - Hussmann | 0 | 0
Wrong program | Wrong program | 1 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
Group | Total | After | Tiebreak | First group row
Ref. leak/ Low charge | 0 | 0 | 0.00025
Doors | 14 | 1 | 14.0002
Drain tube blocked | 3 | 0 | 3.0002
Wrong / Loose wiring | 2 | 2 | 2.0002
Communication problem | 0 | 0 | 0.00021
High Store RH | 5 | 2 | 5.0002
Enclosure Seal | 0 | 0 | 0.00019
Component Failure | 0 | 0 | 0.00018
Defrost Sync | 0 | 0 | 0.00017
False Alarm | 5 | 2 | 5.0002
Setpoint change | 0 | 0 | 0.00015
Overstocking | 2 | 2 | 2.0001
Double defrost | 0 | 0 | 0.00013
Return Air blocked | 0 | 0 | 0.00012
Unidentified air leak | 0 | 0 | 0.00011
Freedom | 0 | 0 | 0.0001
Heavy case load | 0 | 0 | 9e-05
Installation issue | 2 | 0 | 2.0001
Unknown | 2 | 2 | 2.0001
Program change - Hussmann | 0 | 0 | 6e-05
Wrong program | 1 | 0 | 1.0001
Ranked group | After | Before | Total
Doors | 1 | 13 | 14
High Store RH | 2 | 3 | 5
False Alarm | 2 | 3 | 5
Drain tube blocked | 0 | 3 | 3
Wrong / Loose wiring | 2 | 0 | 2
Overstocking | 2 | 0 | 2
Installation issue | 0 | 2 | 2
Unknown | 2 | 0 | 2
Wrong program | 0 | 1 | 1
Ref. leak/ Low charge | 0 | 0 | 0
Communication problem | 0 | 0 | 0
Enclosure Seal | 0 | 0 | 0
Component Failure | 0 | 0 | 0
Defrost Sync | 0 | 0 | 0
Setpoint change | 0 | 0 | 0
Double defrost | 0 | 0 | 0
Return Air blocked | 0 | 0 | 0
Unidentified air leak | 0 | 0 | 0
Freedom | 0 | 0 | 0
Heavy case load | 0 | 0 | 0
Program change - Hussmann | 0 | 0 | 0
Ranked group | Ref. leak/ Low charge | Doors | Drain tube blocked | Wrong / Loose wiring | Communication problem | High Store RH | Enclosure Seal | Component Failure | Defrost Sync | False Alarm | Setpoint change | Overstocking | Double defrost | Return Air blocked | Unidentified air leak | Freedom | Heavy case load | Installation issue | Unknown | Program change - Hussmann | Wrong program
Doors |  | 1
High Store RH | [5 empty] | 2
False Alarm | [9 empty] | 2
Drain tube blocked
Wrong / Loose wiring |  |  |  | 2
Overstocking | [11 empty] | 2
Installation issue
Unknown | [18 empty] | 2
Wrong program
Ref. leak/ Low charge
Communication problem
Enclosure Seal
Component Failure
Defrost Sync
Setpoint change
Double defrost
Return Air blocked
Unidentified air leak
Freedom
Heavy case load
Program change - Hussmann
Chart 7 title | RLN3MA - issues after vs before clean point (Jun 1 to Jul 22)
T12. RLN2MA - after vs before by group
Prefix from cell below; filters Summary by serial prefix + timeline; feeds Chart 8 via ch*.
Nomenclature: | RLN2MA
Root Cause | Group | Total | After
Ref. leak/ Low charge | Ref. leak/ Low charge | 0 | 0
Door Torque | Doors | 3 | 0
Door Gasket | Doors | 2 | 0
Door frame heater | Doors | 0 | 0
Door Torsion rod | Doors | 0 | 0
Door not closed (Overnight) | Doors | 3 | 0
Door - general | Doors | 0 | 0
Drain tube blocked | Drain tube blocked | 0 | 0
Wrong / Loose wiring | Wrong / Loose wiring | 0 | 0
Communication problem | Communication problem | 4 | 0
High Store RH | High Store RH | 3 | 1
Enclosure Seal | Enclosure Seal | 0 | 0
Component Failure | Component Failure | 2 | 2
Defrost Sync | Defrost Sync | 0 | 0
False Alarm | False Alarm | 2 | 1
Setpoint change | Setpoint change | 0 | 0
Overstocking | Overstocking | 1 | 1
Double defrost | Double defrost | 0 | 0
Return Air blocked | Return Air blocked | 0 | 0
Unidentified air leak | Unidentified air leak | 0 | 0
Freedom | Freedom | 1 | 1
Heavy case load | Heavy case load | 0 | 0
Installation issue | Installation issue | 0 | 0
Unknown | Unknown | 1 | 1
Program change - Hussmann | Program change - Hussmann | 0 | 0
Wrong program | Wrong program | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
Group | Total | After | Tiebreak | First group row
Ref. leak/ Low charge | 0 | 0 | 0.00025
Doors | 8 | 0 | 8.0002
Drain tube blocked | 0 | 0 | 0.00023
Wrong / Loose wiring | 0 | 0 | 0.00022
Communication problem | 4 | 0 | 4.0002
High Store RH | 3 | 1 | 3.0002
Enclosure Seal | 0 | 0 | 0.00019
Component Failure | 2 | 2 | 2.0002
Defrost Sync | 0 | 0 | 0.00017
False Alarm | 2 | 1 | 2.0002
Setpoint change | 0 | 0 | 0.00015
Overstocking | 1 | 1 | 1.0001
Double defrost | 0 | 0 | 0.00013
Return Air blocked | 0 | 0 | 0.00012
Unidentified air leak | 0 | 0 | 0.00011
Freedom | 1 | 1 | 1.0001
Heavy case load | 0 | 0 | 9e-05
Installation issue | 0 | 0 | 8e-05
Unknown | 1 | 1 | 1.0001
Program change - Hussmann | 0 | 0 | 6e-05
Wrong program | 0 | 0 | 5e-05
Ranked group | After | Before | Total
Doors | 0 | 8 | 8
Communication problem | 0 | 4 | 4
High Store RH | 1 | 2 | 3
Component Failure | 2 | 0 | 2
False Alarm | 1 | 1 | 2
Overstocking | 1 | 0 | 1
Freedom | 1 | 0 | 1
Unknown | 1 | 0 | 1
Ref. leak/ Low charge | 0 | 0 | 0
Drain tube blocked | 0 | 0 | 0
Wrong / Loose wiring | 0 | 0 | 0
Enclosure Seal | 0 | 0 | 0
Defrost Sync | 0 | 0 | 0
Setpoint change | 0 | 0 | 0
Double defrost | 0 | 0 | 0
Return Air blocked | 0 | 0 | 0
Unidentified air leak | 0 | 0 | 0
Heavy case load | 0 | 0 | 0
Installation issue | 0 | 0 | 0
Program change - Hussmann | 0 | 0 | 0
Wrong program | 0 | 0 | 0
Ranked group | Ref. leak/ Low charge | Doors | Drain tube blocked | Wrong / Loose wiring | Communication problem | High Store RH | Enclosure Seal | Component Failure | Defrost Sync | False Alarm | Setpoint change | Overstocking | Double defrost | Return Air blocked | Unidentified air leak | Freedom | Heavy case load | Installation issue | Unknown | Program change - Hussmann | Wrong program
Doors
Communication problem
High Store RH | [5 empty] | 1
Component Failure | [7 empty] | 2
False Alarm | [9 empty] | 1
Overstocking | [11 empty] | 1
Freedom | [15 empty] | 1
Unknown | [18 empty] | 1
Ref. leak/ Low charge
Drain tube blocked
Wrong / Loose wiring
Enclosure Seal
Defrost Sync
Setpoint change
Double defrost
Return Air blocked
Unidentified air leak
Heavy case load
Installation issue
Program change - Hussmann
Wrong program
Chart 8 title | RLN2MA - issues after vs before clean point (Jun 1 to Jul 22)
T13. RMN4MA - after vs before by group
Prefix from cell below; filters Summary by serial prefix + timeline; feeds Chart 9 via ch*.
Nomenclature: | RMN4MA
Root Cause | Group | Total | After
Ref. leak/ Low charge | Ref. leak/ Low charge | 2 | 1
Door Torque | Doors | 1 | 1
Door Gasket | Doors | 0 | 0
Door frame heater | Doors | 0 | 0
Door Torsion rod | Doors | 0 | 0
Door not closed (Overnight) | Doors | 3 | 1
Door - general | Doors | 1 | 1
Drain tube blocked | Drain tube blocked | 0 | 0
Wrong / Loose wiring | Wrong / Loose wiring | 0 | 0
Communication problem | Communication problem | 0 | 0
High Store RH | High Store RH | 1 | 1
Enclosure Seal | Enclosure Seal | 0 | 0
Component Failure | Component Failure | 0 | 0
Defrost Sync | Defrost Sync | 0 | 0
False Alarm | False Alarm | 4 | 2
Setpoint change | Setpoint change | 0 | 0
Overstocking | Overstocking | 0 | 0
Double defrost | Double defrost | 0 | 0
Return Air blocked | Return Air blocked | 0 | 0
Unidentified air leak | Unidentified air leak | 0 | 0
Freedom | Freedom | 1 | 1
Heavy case load | Heavy case load | 0 | 0
Installation issue | Installation issue | 2 | 0
Unknown | Unknown | 0 | 0
Program change - Hussmann | Program change - Hussmann | 0 | 0
Wrong program | Wrong program | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
Group | Total | After | Tiebreak | First group row
Ref. leak/ Low charge | 2 | 1 | 2.0002
Doors | 5 | 3 | 5.0002
Drain tube blocked | 0 | 0 | 0.00023
Wrong / Loose wiring | 0 | 0 | 0.00022
Communication problem | 0 | 0 | 0.00021
High Store RH | 1 | 1 | 1.0002
Enclosure Seal | 0 | 0 | 0.00019
Component Failure | 0 | 0 | 0.00018
Defrost Sync | 0 | 0 | 0.00017
False Alarm | 4 | 2 | 4.0002
Setpoint change | 0 | 0 | 0.00015
Overstocking | 0 | 0 | 0.00014
Double defrost | 0 | 0 | 0.00013
Return Air blocked | 0 | 0 | 0.00012
Unidentified air leak | 0 | 0 | 0.00011
Freedom | 1 | 1 | 1.0001
Heavy case load | 0 | 0 | 9e-05
Installation issue | 2 | 0 | 2.0001
Unknown | 0 | 0 | 7e-05
Program change - Hussmann | 0 | 0 | 6e-05
Wrong program | 0 | 0 | 5e-05
Ranked group | After | Before | Total
Doors | 3 | 2 | 5
False Alarm | 2 | 2 | 4
Ref. leak/ Low charge | 1 | 1 | 2
Installation issue | 0 | 2 | 2
High Store RH | 1 | 0 | 1
Freedom | 1 | 0 | 1
Drain tube blocked | 0 | 0 | 0
Wrong / Loose wiring | 0 | 0 | 0
Communication problem | 0 | 0 | 0
Enclosure Seal | 0 | 0 | 0
Component Failure | 0 | 0 | 0
Defrost Sync | 0 | 0 | 0
Setpoint change | 0 | 0 | 0
Overstocking | 0 | 0 | 0
Double defrost | 0 | 0 | 0
Return Air blocked | 0 | 0 | 0
Unidentified air leak | 0 | 0 | 0
Heavy case load | 0 | 0 | 0
Unknown | 0 | 0 | 0
Program change - Hussmann | 0 | 0 | 0
Wrong program | 0 | 0 | 0
Ranked group | Ref. leak/ Low charge | Doors | Drain tube blocked | Wrong / Loose wiring | Communication problem | High Store RH | Enclosure Seal | Component Failure | Defrost Sync | False Alarm | Setpoint change | Overstocking | Double defrost | Return Air blocked | Unidentified air leak | Freedom | Heavy case load | Installation issue | Unknown | Program change - Hussmann | Wrong program
Doors |  | 3
False Alarm | [9 empty] | 2
Ref. leak/ Low charge | 1
Installation issue
High Store RH | [5 empty] | 1
Freedom | [15 empty] | 1
Drain tube blocked
Wrong / Loose wiring
Communication problem
Enclosure Seal
Component Failure
Defrost Sync
Setpoint change
Overstocking
Double defrost
Return Air blocked
Unidentified air leak
Heavy case load
Unknown
Program change - Hussmann
Wrong program
Chart 9 title | RMN4MA - issues after vs before clean point (Jun 1 to Jul 22)

## Counts (hidden)
Counts - list line and group rollups
Root Cause | Group | Total Lines | Visible Lines | After Clean Point | Clean-Point Date | Group | Total Lines | Visible Lines | After Clean Point
Ref. leak/ Low charge | Ref. leak/ Low charge | 13 | 0 | 2 | 2026-04-20 | Ref. leak/ Low charge | 13 | 0 | 2
Door Torque | Doors | 13 | 0 | 1 | 2026-06-05 | Doors | 44 | 0 | 6
Door Gasket | Doors | 5 | 0 | 0 | 2026-06-05 | Drain tube blocked | 12 | 0 | 0
Door frame heater | Doors | 5 | 0 | 0 | 2026-06-05 | Wrong / Loose wiring | 7 | 0 | 2
Door Torsion rod | Doors | 1 | 0 | 1 | 2026-06-05 | Communication problem | 10 | 0 | 1
Door not closed (Overnight) | Doors | 13 | 0 | 2 | 2026-06-05 | High Store RH | 13 | 1 | 4
Door - general | Doors | 7 | 0 | 2 | 2026-06-05 | Enclosure Seal | 3 | 0 | 0
Drain tube blocked | Drain tube blocked | 12 | 0 | 0 | 2026-07-10 | Component Failure | 6 | 0 | 6
Wrong / Loose wiring | Wrong / Loose wiring | 7 | 0 | 2 | 2026-03-27 | Defrost Sync | 4 | 0 | 0
Communication problem | Communication problem | 10 | 0 | 1 | 2026-06-18 | False Alarm | 16 | 0 | 5
High Store RH | High Store RH | 13 | 1 | 4 | 2026-05-29 | Setpoint change | 1 | 0 | 1
Enclosure Seal | Enclosure Seal | 3 | 0 | 0 | 2026-04-23 | Overstocking | 4 | 0 | 3
Component Failure | Component Failure | 6 | 0 | 6 | 2026-03-01 | Double defrost | 1 | 0 | 0
Defrost Sync | Defrost Sync | 4 | 0 | 0 | 2026-06-12 | Return Air blocked | 1 | 0 | 0
False Alarm | False Alarm | 16 | 0 | 5 | 2026-05-22 | Unidentified air leak | 2 | 0 | 0
Setpoint change | Setpoint change | 1 | 0 | 1 | 2026-03-16 | Freedom | 6 | 0 | 5
Overstocking | Overstocking | 4 | 0 | 3 | 2026-05-29 | Heavy case load | 1 | 0 | 0
Double defrost | Double defrost | 1 | 0 | 0 | 2026-05-29 | Installation issue | 9 | 0 | 2
Return Air blocked | Return Air blocked | 1 | 0 | 0 | 2026-05-29 | Unknown | 7 | 0 | 7
Unidentified air leak | Unidentified air leak | 2 | 0 | 0 | 2026-06-16 | Program change - Hussmann | 1 | 0 | 0
Freedom | Freedom | 6 | 0 | 5 | 2026-03-01 | Wrong program | 4 | 0 | 0
Heavy case load | Heavy case load | 1 | 0 | 0 | 2026-05-29 | Value | 0 | 0 | 0
Installation issue | Installation issue | 9 | 0 | 2 | 2026-05-29 | 240 | 0 | 0 | 0
Unknown | Unknown | 7 | 0 | 7 | 2026-03-01 | 400 | 0 | 0 | 0
Program change - Hussmann | Program change - Hussmann | 1 | 0 | 0 | 2026-05-29 | 80 | 0 | 0 | 0
Wrong program | Wrong program | 4 | 0 | 0 | 0
0 | 0 | 83 | 0 | 0 | 0
0 | 0 | 83 | 0 | 0 | 0
0 | 0 | 83 | 0 | 0 | 0
0 | 0 | 83 | 0 | 0 | 0
0 | 0 | 83 | 0 | 0 | 0
0 | 0 | 83 | 0 | 0 | 0
0 | 0 | 83 | 0 | 0 | 0
0 | 0 | 83 | 0 | 0 | 0
0 | 0 | 83 | 0 | 0 | 0
0 | 0 | 83 | 0 | 0 | 0
0 | 0 | 83 | 0 | 0 | 0
0 | 0 | 83 | 0 | 0 | 0
0 | 0 | 83 | 0 | 0 | 0
0 | 0 | 83 | 0 | 0 | 0
0 | 0 | 83 | 0 | 0 | 0
0 | 0 | 83 | 0 | 0 | 0
0 | 0 | 83 | 0 | 0 | 0
0 | 0 | 83 | 0 | 0 | 0
0 | 0 | 83 | 0 | 0 | 0
0 | 0 | 83 | 0 | 0 | 0
0 | 0 | 83 | 0 | 0 | 0
0 | 0 | 83 | 0 | 0 | 0
0 | 0 | 83 | 0 | 0 | 0
0 | 0 | 83 | 0 | 0 | 0
0 | 0 | 83 | 0 | 0 | 0
0 | 0 | 83 | 0 | 0 | 0
0 | 0 | 83 | 0 | 0 | 0
0 | 0 | 83 | 0 | 0 | 0
0 | 0 | 83 | 0 | 0 | 0
0 | 0 | 83 | 0 | 0 | 0

## Graphs (hidden)
Graphs — right-click a chart → Copy → Paste as Picture into PowerPoint | [6 empty] | Issues by root cause (Jun 1 to Jul 22) | [19 empty] | 03/02 | 03/09 | 6 | 4
[7 empty] | Issues after clean point (Jun 1 to Jul 22) | [19 empty] | 03/09 | 03/16 | 7 | 3
From: | 2026-06-01 | ← blank = from the very first call |  |  |  |  | Dispatch by store commission week (by cause group) | [19 empty] | 03/16 | 03/23 | 25 | 2
To: | 2026-07-22 | ← blank = through the latest call |  |  |  |  | Dispatch by call week (by root cause) | [15 empty] | 4 |  |  |  | 03/23 | 03/30 | 16 | 4
Period: | Jun 1 to Jul 22 | [21 empty] | 5 | 5 |  |  | 03/30 | 04/06 | 4 | 9
[7 empty] | Issues by root cause - after vs before clean point (Jun 1 to Jul 22) | [16 empty] | 6 |  |  | 04/06 | 04/13 | 15 | 16
Root Cause | Issues | After clean |  | Root Cause | After clean | [18 empty] | 7 |  |  | 04/13 | 04/20 | 17 | 8
Door not closed (Overnight) | 13 | 2 |  | False Alarm | 5 |  |  | Ref. leak/ Low charge | 4 | 2 | 4.0004 | 2.0004 | Ref. leak/ Low charge | Ref. leak/ Low charge | 4 | 2 | 4.0003 | 2.0002 | Doors | 32 | Doors | 6 |  | 8 | 1 |  | 04/20 | 04/27 | 6 | 1
False Alarm | 12 | 5 |  | Unknown | 5 |  |  | Door Torque | 7 | 1 | 7.0004 | 1.0004 | Doors | Doors | 32 | 6 | 32.0002 | 6.0002 | False Alarm | 12 | False Alarm | 5 |  | 9 | 6 | 9 | 04/27 | 05/04 | 7 | 5
High Store RH | 9 | 4 |  | High Store RH | 4 |  |  | Door Gasket | 5 | 0 | 5.0004 | 0.00038 | Doors | Drain tube blocked | 5 | 0 | 5.0002 | 0.00023 | High Store RH | 9 | Unknown | 5 |  | 10 | 1 |  | 05/04 | 05/11 | 10 | 11
Door Torque | 7 | 1 |  | Overstocking | 3 |  |  | Door frame heater | 4 | 0 | 4.0004 | 0.00037 | Doors | Wrong / Loose wiring | 2 | 2 | 2.0002 | 2.0002 | Installation issue | 6 | High Store RH | 4 | 11 |  | 1 |  | 05/11 | 05/18 | 2 | 4
Installation issue | 6 | 2 |  | Ref. leak/ Low charge | 2 |  |  | Door Torsion rod | 1 | 1 | 1.0004 | 1.0004 | Doors | Communication problem | 5 | 1 | 5.0002 | 1.0002 | Drain tube blocked | 5 | Overstocking | 3 | 12 |  | 1 |  | 05/18 | 05/25 | 5 | 6
Door Gasket | 5 | 0 |  | Door not closed (Overnight) | 2 |  |  | Door not closed (Overnight) | 13 | 2 | 13.0003 | 2.0004 | Doors | High Store RH | 9 | 4 | 9.0002 | 4.0002 | Communication problem | 5 | Ref. leak/ Low charge | 2 | 13 |  | 1 |  | 05/25 | 06/01 | 6 | 8
Drain tube blocked | 5 | 0 |  | Door - general | 2 |  |  | Door - general | 2 | 2 | 2.0003 | 2.0003 | Doors | Enclosure Seal | 0 | 0 | 0.00019 | 0.00019 | Unknown | 5 | Wrong / Loose wiring | 2 | 14 |  | 1 |  | 06/01 | 06/08 | 2 | 15
Communication problem | 5 | 1 |  | Wrong / Loose wiring | 2 |  |  | Drain tube blocked | 5 | 0 | 5.0003 | 0.00033 | Drain tube blocked | Component Failure | 2 | 2 | 2.0002 | 2.0002 | Ref. leak/ Low charge | 4 | Component Failure | 2 | 15 |  | 1 |  | 06/08 | 06/15 | 3 | 8
Unknown | 5 | 5 |  | Component Failure | 2 |  |  | Wrong / Loose wiring | 2 | 2 | 2.0003 | 2.0003 | Wrong / Loose wiring | Defrost Sync | 0 | 0 | 0.00017 | 0.00017 | Overstocking | 3 | Freedom | 2 | 16 |  | 1 |  | 06/15 | 06/22 | 8 | 13
Ref. leak/ Low charge | 4 | 2 |  | Freedom | 2 |  |  | Communication problem | 5 | 1 | 5.0003 | 1.0003 | Communication problem | False Alarm | 12 | 5 | 12.0002 | 5.0002 | Wrong / Loose wiring | 2 | Installation issue | 2 | 17 |  | 1 |  | 06/22 | 06/29 | 4 | 12
Door frame heater | 4 | 0 |  | Installation issue | 2 |  |  | High Store RH | 9 | 4 | 9.0003 | 4.0003 | High Store RH | Setpoint change | 1 | 1 | 1.0002 | 1.0002 | Component Failure | 2 | Communication problem | 1 | 18 |  | 1 |  | 06/29 | 07/06 | 5 | 18
Overstocking | 3 | 3 |  | Door Torque | 1 |  |  | Enclosure Seal | 0 | 0 | 0.00029 | 0.00029 | Enclosure Seal | Overstocking | 3 | 3 | 3.0001 | 3.0001 | Freedom | 2 | Setpoint change | 1 | 19 |  | 1 |  | 07/06 | 07/13 | 5 | 14
Door - general | 2 | 2 |  | Door Torsion rod | 1 |  |  | Component Failure | 2 | 2 | 2.0003 | 2.0003 | Component Failure | Double defrost | 0 | 0 | 0.00013 | 0.00013 | Setpoint change | 1 | Drain tube blocked | 0 | 20 |  | 1 |  | 07/13 | 07/20 | 2 | 0
Wrong / Loose wiring | 2 | 2 |  | Communication problem | 1 |  |  | Defrost Sync | 0 | 0 | 0.00027 | 0.00027 | Defrost Sync | Return Air blocked | 0 | 0 | 0.00012 | 0.00012 | Wrong program | 1 | Enclosure Seal | 0 | 21 |  | 1
Component Failure | 2 | 2 |  | Setpoint change | 1 |  |  | False Alarm | 12 | 5 | 12.0003 | 5.0003 | False Alarm | Unidentified air leak | 0 | 0 | 0.00011 | 0.00011 | Enclosure Seal | 0 | Defrost Sync | 0 | 22 |  | 1
Freedom | 2 | 2 |  | Door Gasket | 0 |  |  | Setpoint change | 1 | 1 | 1.0003 | 1.0003 | Setpoint change | Freedom | 2 | 2 | 2.0001 | 2.0001 | Defrost Sync | 0 | Double defrost | 0 | 23 |  | 1
Door Torsion rod | 1 | 1 |  | Door frame heater | 0 |  |  | Overstocking | 3 | 3 | 3.0002 | 3.0002 | Overstocking | Heavy case load | 0 | 0 | 9e-05 | 9e-05 | Double defrost | 0 | Return Air blocked | 0 | 24 |  | 1
Setpoint change | 1 | 1 |  | Drain tube blocked | 0 |  |  | Double defrost | 0 | 0 | 0.00023 | 0.00023 | Double defrost | Installation issue | 6 | 2 | 6.0001 | 2.0001 | Return Air blocked | 0 | Unidentified air leak | 0 | 25 |  | 1
Wrong program | 1 | 0 |  | Enclosure Seal | 0 |  |  | Return Air blocked | 0 | 0 | 0.00022 | 0.00022 | Return Air blocked | Unknown | 5 | 5 | 5.0001 | 5.0001 | Unidentified air leak | 0 | Heavy case load | 0 | 26 |  | 1
Enclosure Seal | 0 | 0 |  | Defrost Sync | 0 |  |  | Unidentified air leak | 0 | 0 | 0.00021 | 0.00021 | Unidentified air leak | Program change - Hussmann | 0 | 0 | 6e-05 | 6e-05 | Heavy case load | 0 | Program change - Hussmann | 0 | 27 |  | 1
Defrost Sync | 0 | 0 |  | Double defrost | 0 |  |  | Freedom | 2 | 2 | 2.0002 | 2.0002 | Freedom | Wrong program | 1 | 0 | 1.0001 | 5e-05 | Program change - Hussmann | 0 | Wrong program | 0 | 28 |  | 1
Double defrost | 0 | 0 |  | Return Air blocked | 0 |  |  | Heavy case load | 0 | 0 | 0.00019 | 0.00019 | Heavy case load | Value | 0 | 0 | 4e-05 | 4e-05 | Value | 0 | Value | 0 | 29 |  | 1
Return Air blocked | 0 | 0 |  | Unidentified air leak | 0 |  |  | Installation issue | 6 | 2 | 6.0002 | 2.0002 | Installation issue | 240 | 0 | 0 | 3e-05 | 3e-05 | 240 | 0 | 240 | 0 |  |  | 1
Unidentified air leak | 0 | 0 |  | Heavy case load | 0 |  |  | Unknown | 5 | 5 | 5.0002 | 5.0002 | Unknown | 400 | 0 | 0 | 2e-05 | 2e-05 | 400 | 0 | 400 | 0 |  |  | 1
Heavy case load | 0 | 0 |  | Program change - Hussmann | 0 |  |  | Program change - Hussmann | 0 | 0 | 0.00016 | 0.00016 | Program change - Hussmann | 80 | 0 | 0 | 1e-05 | 1e-05 | 80 | 0 | 80 | 0 |  |  | 1
Program change - Hussmann | 0 | 0 |  | Wrong program | 0 |  |  | Wrong program | 1 | 0 | 1.0002 | 0.00015 | Wrong program
Multi-cause group: | Doors | 0 |  | 0 | 0 |  |  | 0 | 0 | 0 | 0.00014 | 0.00014 | 0
Members: | Door Torque | Door Gasket | Door frame heater | Door Torsion rod | Door not closed (Overnight) | Door - general |  | 0 | 0 | 0 | 0.00013 | 0.00013 | 0
Doors = Door Torque + Door Gasket + Door frame heater + Door Torsion rod + Door not closed (Overnight) + Door - general | 0 | 0 |  | 0 | 0 |  |  | 0 | 0 | 0 | 0.00012 | 0.00012 | 0
0 | 0 | 0 |  | 0 | 0 |  |  | 0 | 0 | 0 | 0.00011 | 0.00011 | 0
0 | 0 | 0 |  | 0 | 0 |  |  | 0 | 0 | 0 | 0.0001 | 0.0001 | 0
0 | 0 | 0 |  | 0 | 0 |  |  | 0 | 0 | 0 | 9e-05 | 9e-05 | 0
0 | 0 | 0 |  | 0 | 0 |  |  | 0 | 0 | 0 | 8e-05 | 8e-05 | 0 | [19 empty] | Before / at clean point |  | False Alarm | Door Torque | Door not closed (Overnight) | Ref. leak/ Low charge | Communication problem | Drain tube blocked | High Store RH | DG Installation issue | Unknown | Wrong / Loose wiring | Component Failure | Door - general | Freedom | Defrost Sync | Incorrect Program | Door Gasket | Door frame heater | Enclosure Seal | Overstocking | Unidentified air leak | Case End Seal | Door Torsion rod | Heavy case load | Program change - Hussmann | Return Air blocked |  |  |  |  | Doors | False Alarm | High Store RH | Installation issue | Drain tube blocked | Communication problem | Unknown | Ref. leak/ Low charge | Overstocking | Wrong / Loose wiring | Component Failure | Freedom | Setpoint change | Wrong program | Enclosure Seal | Defrost Sync | Double defrost | Return Air blocked | Unidentified air leak | Heavy case load | Program change - Hussmann | Value | 240 | 400 | 80
0 | 0 | 0 |  | 0 | 0 |  |  | 0 | 0 | 0 | 7e-05 | 7e-05 | 0 | [17 empty] | False Alarm | 5 | 7 | 12 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Doors | 6 | 26 | 32 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 |  | 0 | 0 |  |  | 0 | 0 | 0 | 6e-05 | 6e-05 | 0 | [17 empty] | Door Torque | 1 | 6 | 7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | False Alarm | 5 | 7 | 12 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 |  | 0 | 0 |  |  | 0 | 0 | 0 | 5e-05 | 5e-05 | 0 | [17 empty] | Door not closed (Overnight) | 2 | 11 | 13 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | High Store RH | 4 | 5 | 9 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 |  | 0 | 0 |  |  | 0 | 0 | 0 | 4e-05 | 4e-05 | 0 | [17 empty] | Ref. leak/ Low charge | 2 | 2 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Installation issue | 2 | 4 | 6 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 |  | 0 | 0 |  |  | 0 | 0 | 0 | 3e-05 | 3e-05 | 0 | [17 empty] | Communication problem | 1 | 4 | 5 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Drain tube blocked | 0 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 |  | 0 | 0 |  |  | 0 | 0 | 0 | 2e-05 | 2e-05 | 0 | [17 empty] | Drain tube blocked | 0 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Communication problem | 1 | 4 | 5 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 |  | 0 | 0 |  |  | 0 | 0 | 0 | 1e-05 | 1e-05 | 0 | [17 empty] | High Store RH | 4 | 5 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Unknown | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | DG Installation issue | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Ref. leak/ Low charge | 2 | 2 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | Unknown | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Overstocking | 3 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | Wrong / Loose wiring | 2 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Wrong / Loose wiring | 2 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | Component Failure | 2 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Component Failure | 2 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | Door - general | 2 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Freedom | 2 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | Freedom | 2 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Setpoint change | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | Defrost Sync | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Wrong program | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | Incorrect Program | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Enclosure Seal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | Door Gasket | 0 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Defrost Sync | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | Door frame heater | 0 | 4 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Double defrost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | Enclosure Seal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Return Air blocked | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | Overstocking | 3 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | Unidentified air leak | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | Unidentified air leak | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Heavy case load | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | Case End Seal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Program change - Hussmann | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | Door Torsion rod | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Value | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | Heavy case load | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[23 empty] | 88 | [7 empty] | Setpoint change | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[23 empty] | 89 | [7 empty] | Return Air blocked | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90
91
92
93

## Case Nomenclature Graph (hidden)
Case Nomenclature | Issues
RLN2MA | 22
RLN3MA | 36
RLN4MA | 3
RMN3MA | 7
RMN4MA | 15
RMN5MA | 5
From date | 46174
To date | 46225